## Instructions
Ormeau Facility Asset Control Assessment Workbook
WORKSHOP INSTRUCTIONS:
1. Use this workbook to assess each asset and determine applicable security controls
2. Focus on assets based on their criticality and target Security Level (SL-T)
3. For each asset, answer the characteristic questions to determine which controls apply
4. Document any asset-specific considerations in the notes section
5. Review the automatically populated relevant controls based on asset characteristics
DEFINITIONS:
Security Level 1 (SL-1): Protection against casual or coincidental violation
Security Level 2 (SL-2): Protection against intentional violation using simple means
Security Level 3 (SL-3): Protection against intentional violation using sophisticated means
Security Level 4 (SL-4): Protection against intentional violation using sophisticated means with extended resources
NOTES:
- Not all controls will be applicable to every asset
- Consider the asset's operational context and integration with other systems
- Document assumptions that influence control applicability
- The goal is to create a practical, implementable security control baseline for each asset

## Security Levels
Security Level | Description | Protection Against | Means | Resources | Skills | Motivation
SL-1 | Basic protection | Casual or coincidental violation | Simple | Individual | Generic | Low
SL-2 | Enhanced protection | Intentional violation using simple means | Simple | Few | Generic | Low
SL-3 | Advanced protection | Intentional violation using sophisticated means | Sophisticated | Moderate | Specific | Moderate
SL-4 | Maximum protection | Intentional violation using sophisticated means with extended resources | Sophisticated | Extended | Specific | High
Notes:
1. Different assets may require different SLs depending on their criticality and risk exposure
2. Security requirements compliance increases with higher SLs
3. Not all assets need to achieve SL-4; target SLs should be realistic and risk-based
4. For the Ormeau facility, most assets will likely fall into SL-2 or SL-3 range

## Workshop Guide
WORKSHOP FACILITATION GUIDE
PREPARATION:
1. Pre-populate the Asset List sheet with known assets from the Ormeau Asset Registry
2. Identify key stakeholders who need to participate (system owners, security team, operations)
3. Schedule 2-3 hour blocks with subject matter experts for each functional area
4. Distribute the workbook in advance to allow preliminary review
WORKSHOP PROCESS:
1. Introduction (15 minutes)
- Explain the purpose and process of the workshop
- Review the security levels and requirements framework
- Clarify roles and expectations
2. Asset Prioritization (30 minutes)
- Review the Asset List and validate the information
- Confirm or adjust preliminary Target SLs based on criticality
- Prioritize assets for detailed assessment starting with highest criticality
3. Asset Characteristic Assessment (15 minutes per asset)
- For each asset, create a copy of the Assessment Template sheet
- Work through the Asset Characteristics questions systematically
- Document YES/NO answers and relevant notes
4. Control Applicability Determination (15 minutes per asset)
- Based on characteristics, determine which Fundamental Requirements apply
- Review the specific Security Requirements within each FR (Including relevant (SE)s
- Document applicability and any asset-specific considerations
5. Validation and Gap Analysis (10 minutes per asset)
- Review the automatically identified MITRE TTPs addressed
- Identify any gaps in coverage for the asset's threat profile
- Document additional considerations or custom controls needed
6. Summary and Next Steps (30 minutes)
- Complete the Control Assessment Summary sheet
- Identify common patterns and control requirements
- Establish follow-up actions and implementation planning
FACILITATION TIPS:
- Keep discussions focused on the specific asset characteristics and controls
- Use the sample assessment as a reference for how to complete each section
- For complex systems, consider breaking down into component assets
- Document assumptions clearly to support future security assessments
- Encourage participants to provide context about operational constraints
- Focus on practical, implementable controls appropriate to the target SL
- Remember the goal is to identify relevant controls, not to implement them during the workshop

## Workhop Asset List
Asset ID | Asset Name | Asset Description | Zone | Criticality Rating | Safety Impact | Preliminary Target SL
DOW_04 | Site Radio DMR | Digital Mobile Radio system for site communications | Communications Zone | 3 | Yes | SL-2
DOW_06 | Perimeter Intrusion Detection System | PIDS system for perimeter security monitoring
DOW_07 | Depot CCTV | CCTV system for security monitoring | Security Zone | 2 | No | SL-2
DOW_08 | Intercommunications System | Intercom system for comms between gatehouse and maintenance facility
DOW_09 | Access Control System | Physical access control system | Security Zone | 3 | Yes | SL-2
DOW_10 | Uninteruptable Power Supply | UPS
DOW_20 | Lighting | Sitewide KNX controlled lighting
DOW_21 | Emergency Lighting | Emergency lighting system | Safety Zone | 4 | Yes | SL-3
DOW_22 | Energy Management System | System for monitoring and managing energy usage | Facility Zone | 2 | No | SL-2
DOW_24 | Building Management System | System for monitoring and controlling building systems | Facility Zone | 3 | Yes | SL-2
DOW_25 | Fire Detection System | Fire detection and alarm system | Safety Zone | 5 | Yes | SL-3
DOW_26 | Emergency Warning System
DOW_27 | HVAC | Administration/Office area HVAC
DOW_28 | CRAC | CER HVAC
DOW_32 | OHLE SCADA | Overhead Line Equipment SCADA | OT Control Zone | 5 | Yes | SL-3
DOW_33 | PA System | Sitewide PA System
DOW_38 | HV Transformer | HV Transformer control system
Populate with Assets from Register - What assets do we want to cover - and in what order?

## Decision Tree Logic
CONTROL APPLICABILITY DECISION TREE
This decision tree helps determine which security controls are relevant for each asset based on its characteristics.
Follow the questions in sequence to identify applicable control categories.
1. TARGET SECURITY LEVEL (SL-T)
Question: What is the target Security Level for this asset?
Guidance:
- SL-1: Basic protection against casual or coincidental violation
- SL-2: Protection against intentional violation using simple means
- SL-3: Protection against intentional violation using sophisticated means
- SL-4: Protection against intentional violation using sophisticated means with extended resources
Impact: Higher SL-T requires implementation of more controls and at higher capability
2. CONNECTIVITY
Question: Is the asset connected to a TCP/IP network?
If YES -> Apply SR 1.2 | SR 1.8 | SR 1.9 | SR 1.13 | SR 3.1 | SR 3.2 | SR 4.1 | SR 4.3 | SR 5.1 | SR 5.2 | SR 6.1 | SR 6.2 | SR 7.1 | SR 7.6
Question: Does the asset have wireless capability?
If YES -> Apply SR 2.2 | SR 2.3 | SR 4.3 | SR 6.2 | SR 7.6
Question: Does the asset require remote access?
If YES -> Apply SR 1.1 | SR 1.3 | SR 1.4 | SR 1.5 | SR 1.7 | SR 1.8 | SR 1.9 | SR 1.11 | SR 1.13 | SR 2.1 | SR 2.3 | SR 2.6 | SR 2.7 | SR 3.1 | SR 3.5 | SR 3.8 | SR 4.3 | SR 6.1 | SR 6.2 | SR 7.7
3. USER INTERACTION
Question: Does the asset have user interfaces?
If YES-> Apply SR 1.1 | SR 1.3 | SR 1.4 | SR 1.5 | SR 1.7 | SR 1.11 | SR 2.1 | SR 2.5 | SR 2.7 | SR 3.5 | SR 3.8 | SR 6.1
4. PROGRAMMABILITY
Question: Is the asset programmable?
If YES -> Apply SR 1.2 | SR 2.1 | SR 2.4 | SR 3.3 | SR 3.5 | SR 3.6 | SR 3.7 | SR 7.3 | SR 7.4 | SR 7.7
Question: Does the asset receive firmware updates?
If YES ->Apply SR 3.4 | SR 5.3 | SR 7.3
5. DATA HANDLING
Question: Does the asset store data?
If YES -> Apply SR 3.9 | SR 4.1 | SR 4.2 | SR 4.3 | SR 7.3
6. SAFETY CRITICALITY
Question: Is the asset safety-critical?
If YES -> Apply SR 3.3 | SR 3.6 | SR 3.7 | SR 5.3 | SR 5.4 | SR 7.4 | SR 7.5
7. OPERATING SYSTEM
Question: Does the asset have an operating system?
If YES ->Apply SR 3.2 | SR 3.4 | SR 7.2
8. ALL ASSETS
The following security requirements apply to all assets regardless of characteristics:
SR 7.8 (Control system component inventory)
NOTE: This decision tree provides general guidance. The specific implementation of each control will depend on the asset's context and the target SL.

## enhanced_OMF_DRA_Workshop_Asset
ASSET ASSESSMENT TEMPLATE
ASSET INFORMATION
Asset ID:
Asset Name:
Zone:
Target Security Level (SL-T):
ASSET CHARACTERISTICS |  | YES/NO | NOTES
Operating System?
TCP/IP Network Connected?
Wireless Capability?
Remote Access Required?
User Interfaces Present?
Programmable?
Firmware Updates?
Data Storage?
Safety Critical?
APPLICABLE FUNDAMENTAL REQUIREMENTS |  | APPLICABLE? | RELEVANT SECURITY REQUIREMENTS | SL | RAILWAY IMPLEMENTATION NOTES
FR 1: Identification and authentication control (IAC) |  |  | SR 1.1, SR 1.1 RE(1-3), SR 1.2, SR 1.2 RE(1), SR 1.3, SR 1.3 RE(1), SR 1.4, SR 1.5, SR 1.5 RE(1), SR 1.6, SR 1.6 RE(1), SR 1.7, SR 1.7 RE(1-2), SR 1.8, SR 1.9, SR 1.9 RE(1), SR 1.10, SR 1.11, SR 1.12, SR 1.13, SR 1.13 RE(1) | SL1-SL4, depending on requirement | Railway authentication may leverage existing physical controls where appropriate. External solutions or compensating countermeasures may be necessary for legacy systems. Remote access requires special consideration due to potential safety impacts.
FR 2: Use control (UC) |  |  | SR 2.1, SR 2.1 RE(1-4), SR 2.2, SR 2.2 RE(1), SR 2.3, SR 2.3 RE(1), SR 2.4, SR 2.4 RE(1), SR 2.5, SR 2.6, SR 2.7, SR 2.8, SR 2.8 RE(1), SR 2.9, SR 2.9 RE(1), SR 2.10, SR 2.11, SR 2.11 RE(1-2), SR 2.12, SR 2.12 RE(1) | SL1-SL4, depending on requirement | Session locks and timeouts must be carefully applied with system availability and safety considered. Dual approval mechanisms may require alternative approaches for time-critical functions. Audit logs from distributed systems should be centrally managed with potential time delay consideration.
FR 3: System integrity (SI) |  |  | SR 3.1, SR 3.1 RE(1), SR 3.2, SR 3.2 RE(1-2), SR 3.3, SR 3.3 RE(1-2), SR 3.4, SR 3.4 RE(1), SR 3.5, SR 3.6, SR 3.7, SR 3.8, SR 3.8 RE(1-3), SR 3.9, SR 3.9 RE(1) | SL1-SL4, depending on requirement | Railway systems can utilize compensating controls for integrity protection such as boundary protection and diverse transmission channels. Prevention mechanisms like removable media control may be preferable to detection mechanisms on all embedded devices. Security verification during operation must not interfere with safety functions.
FR 4: Data confidentiality (DC) |  |  | SR 4.1, SR 4.1 RE(1-2), SR 4.2, SR 4.2 RE(1), SR 4.3 | SL1-SL4, depending on requirement | Railway systems should prioritize operational data for confidentiality protection. Cryptographic mechanisms should follow established standards and be properly documented. Current railway applications often lack extensive permission management for data purging purposes.
FR 5: Restricted data flow (RDF) |  |  | SR 5.1, SR 5.1 RE(1-3), SR 5.2, SR 5.2 RE(1-3), SR 5.3, SR 5.3 RE(1), SR 5.4 | SL1-SL4, depending on requirement | Network segmentation should consider operational continuity needs. Physical segregation may be replaced by logical segregation with additional controls. Essential services must continue during incidents. Railway safety architecture may not permit fail-close behaviors that could affect safety functions.
FR 6: Timely response to events (TRE) |  |  | SR 6.1, SR 6.1 RE(1), SR 6.2 | SL1-SL3, depending on requirement | Monitoring must be implemented with consideration for railway operational requirements. System logs should be centrally managed where possible with defined access controls.
FR 7: Resource availability (RA) |  |  | SR 7.1, SR 7.1 RE(1-2), SR 7.2, SR 7.3, SR 7.3 RE(1-2), SR 7.4, SR 7.5, SR 7.6, SR 7.6 RE(1), SR 7.7, SR 7.8 | SL1-SL3, depending on requirement | Railway systems must ensure continuity of safety functions during security events. Recovery and restart procedures must consider safety implications. Configuration management based on baselines is common practice. Emergency power transitions must not affect security state.
MITRE TTPs ADDRESSED BY SELECTED CONTROLS |  |  |  | SL
[Will be populated based on the SR mapping following MIRE_TTP relationships]
ASSET-SPECIFIC CONSIDERATIONS AND RAILWAY CONTEXT
[Document any asset-specific considerations or railway context factors that affect security requirement implementation]
SECURITY LEVEL (SL) IMPLEMENTATION PLAN
SL1 Requirements: | [List all applicable SL1 requirements based on asset characteristics]
SL2 Requirements: | [List all applicable SL2 requirements based on asset characteristics]
SL3 Requirements: | [List all applicable SL3 requirements based on asset characteristics]
SL4 Requirements: | [List all applicable SL4 requirements based on asset characteristics]
COMPENSATING CONTROLS FOR RAILWAY-SPECIFIC CHALLENGES
[Document any compensating controls needed to address railway-specific implementation challenges]
WORKSHOP CONCLUSIONS
[Document final decisions and any follow-up actions]

## MIRE_TTP
TTP ID | Description | Relevant Security Requirements | FR References | Target Asset Characteristics | Railway Notes
T0800 | Activate Firmware Update Mode | SR 1.2, SR 2.1, SR 3.1, SR 5.1 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC), FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF) | Firmware Updates | Firmware update procedures should be documented and controlled with appropriate authentication.
T0809 | Data Destruction | SR 3.9, SR 7.3, SR 7.4 | FR 3 - System integrity (SI), FR 7 - Resource availability (RA) | Data Storage | Railways have strict policies for recovery to ensure both safe and secure states.
T0811 | Data from Information Repositories | SR 4.2 | FR 4 - Data confidentiality (DC) | Data Storage | Data repositories containing railway operational information require access controls and audit logging.
T0812 | Default Credentials | SR 1.1, SR 1.3, SR 1.5, SR 1.7, SR 1.11 | FR 1 - Identification and authentication control (IAC) | User Interfaces, Remote Access | Railways have mostly distributed systems with simple passwords. The full account management requires major change in infrastructure.
T0816 | Device Restart/Shutdown | SR 3.7, SR 5.4, SR 7.1, SR 7.2, SR 7.5 | FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF), FR 7 - Resource availability (RA) | Safety Critical | Device restart in railway systems must consider safety impacts and maintain essential functions.
T0817 | Drive-by Compromise | SR 1.13, SR 3.2, SR 5.2 | FR 1 - Identification and authentication control (IAC), FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF) | TCP/IP Network, User Interfaces | Implement controls at network boundaries and control web browser access to untrusted sites in railway systems.
T0821 | Modify Controller Tasking | SR 3.3, SR 3.5, SR 3.6, SR 7.4 | FR 3 - System integrity (SI), FR 7 - Resource availability (RA) | Programmable, Safety Critical | Safety functions and security functions in railway controllers must be properly segregated.
T0822 | External Remote Services | SR 1.13, SR 2.6, SR 3.8, SR 5.2 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC), FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF) | Remote Access | Remote services should be subject to explicit authorization with defined time limits in railway applications.
T0836 | Modify Parameter | SR 3.6, SR 7.3 | FR 3 - System integrity (SI), FR 7 - Resource availability (RA) | Programmable | Parameter changes in safety-critical railway systems should be subject to verification and authorization.
T0838 | Modify Alarm Settings | SR 3.3, SR 3.6, SR 3.7, SR 5.4 | FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF) | Safety Critical, Programmable | Alarm systems in railway applications must have tamper detection and protection.
T0839 | Module Firmware | SR 3.4, SR 5.3, SR 7.8 | FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF), FR 7 - Resource availability (RA) | Firmware Updates | Firmware integrity is critical for safety systems in railway applications.
T0842 | Network Sniffing | SR 3.1, SR 4.1, SR 4.3, SR 5.1, SR 5.2, SR 6.2 | FR 3 - System integrity (SI), FR 4 - Data confidentiality (DC), FR 5 - Restricted data flow (RDF), FR 6 - Timely response to events (TRE) | TCP/IP Network, Wireless Capability | Segmentation in railway systems should consider operational needs for continued function during incidents.
T0843 | Program Download | SR 7.7 | FR 7 - Resource availability (RA) | Programmable | Program downloads should be subject to integrity checks and authorization in railway systems.
T0845 | Program Upload | SR 7.7 | FR 7 - Resource availability (RA) | Programmable | Code signing and verification is critical for safety-critical railway applications.
T0849 | Masquerading | SR 1.2, SR 1.8, SR 1.9 | FR 1 - Identification and authentication control (IAC) | TCP/IP Network, Remote Access | Identity verification is critical in railway systems, especially for control protocols that may lack built-in authentication.
T0857 | System Firmware | SR 3.4, SR 5.3 | FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF) | Firmware Updates | Railway systems should implement secure firmware update processes with verification.
T0858 | Change Operating Mode | SR 2.1, SR 7.7 | FR 2 - Use control (UC), FR 7 - Resource availability (RA) | Programmable, Safety Critical | Mode changes should be subject to authorization checks and logging in safety-critical railway systems.
T0859 | Valid Accounts | SR 1.1, SR 1.2, SR 1.3, SR 1.4, SR 1.11, SR 2.1, SR 2.7 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC) | User Interfaces, Remote Access | Railway operators should install unique account management systems combined with physical security measures.
T0860 | Wireless Compromise | SR 1.13, SR 2.2, SR 2.3, SR 7.6 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC), FR 7 - Resource availability (RA) | Wireless Capability | Wireless communications in railway systems often require compensating controls beyond the wireless protocol security.
T0861 | Point & Tag Identification | SR 7.8 | FR 7 - Resource availability (RA) | All Assets | Asset inventory in railway systems must include both IT and OT components with appropriate classification.
T0863 | User Execution | SR 2.1, SR 2.5, SR 6.1 | FR 2 - Use control (UC), FR 6 - Timely response to events (TRE) | User Interfaces | Railway user interfaces should implement principle of least privilege based on role requirements.
T0864 | Transient Cyber Asset | SR 2.3, SR 7.8 | FR 2 - Use control (UC), FR 7 - Resource availability (RA) | Remote Access, Wireless Capability | Portable and mobile devices are widely used in railway infrastructure for diagnostic and safety-relevant purposes.
T0865 | Spearphishing Attachment | SR 1.13, SR 2.4, SR 3.2 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC), FR 3 - System integrity (SI) | TCP/IP Network, User Interfaces | Email systems connected to railway control networks require heightened protection.
T0866 | Exploitation of Remote Services
T0867 | Lateral Tool Transfer
T0868 | Detect Operating Mode | SR 7.8 | FR 7 - Resource availability (RA) | Safety Critical, Programmable | Mode transitions in railway systems should be logged and monitored.
T0869 | Standard Application Layer Protocol
T0871 | Execution through API | SR 3.5, SR 7.7 | FR 3 - System integrity (SI), FR 7 - Resource availability (RA) | Programmable, Remote Access | Input validation for railway systems should consider safety implications of invalid inputs.
T0872 | Indicator Removal on Host | SR 3.9, SR 6.1 | FR 3 - System integrity (SI), FR 6 - Timely response to events (TRE) | Operating System, Data Storage | Audit logs for railway systems should be protected with access controls and backup mechanisms.
T0873 | Project File Infection | SR 2.4, SR 3.2, SR 3.4 | FR 2 - Use control (UC), FR 3 - System integrity (SI) | Programmable, Operating System | Prevention means mechanisms such as removable media control, and workstation and laptop management policies, used in conjunction with means of detection at railway system entry points (e.g. USB cleaning stations, IDS, etc.) may be preferred as a compensating security measure.
T0874 | Hooking
T0877 | I/O Image
T0878 | Alarm Supression
T0879 | Damage to Property
T0880 | Loss of Safety
T0881 | Service Stop | SR 5.4, SR 7.1, SR 7.2, SR 7.5 | FR 5 - Restricted data flow (RDF), FR 7 - Resource availability (RA) | Safety Critical, TCP/IP Network | Railway systems should implement fail-safe mechanisms for service stops that maintain safety functions.
T0882 | Theft of Operational Information | SR 2.5, SR 3.8, SR 4.1, SR 4.2, SR 6.1 | FR 2 - Use control (UC), FR 3 - System integrity (SI), FR 4 - Data confidentiality (DC), FR 6 - Timely response to events (TRE) | Data Storage, Remote Access | Data classification is critical in railway systems to identify information that requires protection.
T0883 | Internet Accessible Device
T0884 | Connection Proxy
T0885 | Commonly Used Port | SR 5.1, SR 5.2, SR 6.2, SR 7.6 | FR 5 - Restricted data flow (RDF), FR 6 - Timely response to events (TRE), FR 7 - Resource availability (RA) | TCP/IP Network | Restricted network segments in railway applications should implement extra monitoring and filtering.
T0886 | Remote Services | SR 1.13, SR 2.6 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC) | Remote Access | Remote access to railway systems requires strict controls due to safety implications.
T0887 | Wireless Sniffing | SR 2.2, SR 3.1, SR 4.1, SR 4.3, SR 6.2 | FR 2 - Use control (UC), FR 3 - System integrity (SI), FR 4 - Data confidentiality (DC), FR 6 - Timely response to events (TRE) | Wireless Capability | Wireless communications for railway systems may require additional encryption beyond protocol standards.
T0888 | Remote System Information Discovery
T0889 | Modify Program | SR 3.3, SR 3.4, SR 5.3, SR 7.4 | FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF), FR 7 - Resource availability (RA) | Programmable | Program integrity verification is critical before and after changes in railway applications.
T0890 | Exploitation for Privilege Escalation
T0891 | Hardcoded Credentials | SR 1.1, SR 1.4, SR 1.5, SR 1.7 | FR 1 - Identification and authentication control (IAC) | Firmware Updates, Programmable | Legacy railway systems may require compensating controls if hardcoded credentials cannot be eliminated.
T0893 | Data from Local System | SR 4.1, SR 4.2 | FR 4 - Data confidentiality (DC) | Data Storage | Data leakage prevention measures should be implemented for railway operational data.
T0830 | Adversary-in-the-Middle | SR 1.2, SR 3.1, SR 3.4, SR5.1, SR 6.2, SR 7.7 | FR 1 - Identification and authentication control (IAC), FR 2 - Use control (UC), FR 3 - System integrity (SI), FR 5 - Restricted data flow (RDF), FR 7 - Resource availability (RA)
T0856 | Spoof Reporting Message

## Decision Tree Resultant SR
Category | Question | Guidance | ull
TARGET SECURITY LEVEL (SL-T) | What is the target Security Level for this asset? | SL-1: Basic protection against casual or coincidental violation SL-2: Protection against intentional violation using simple means SL-3: Protection against intentional violation using sophisticated means SL-4: Protection against intentional violation using sophisticated means with extended resources | Higher SL-T requires implementation of more controls and at higher capability
Category | Question | Guidance | Applicable Security Requirments
CONNECTIVITY | Is the asset connected to a TCP/IP network? | Consider all network connections including management interfaces | SR 1.2, SR 1.2 RE(1),SR 1.8, SR 1.9, SR 1.9 RE(1), SR 1.13,SR 1.13 RE(1), SR 3.1, SR 3.1 RE(1), SR 3.2, SR 3.2 RE(1), SR 3.2 RE(2), SR 4.1, SR 4.1 RE(1), SR 4.1 RE(2), SR 4.3, SR 5.1,SR 5.1 RE(1), SR 5.1 RE(2), SR 5.1 RE(3), SR 5.2, SR 5.2 RE(1), SR 5.2 RE(2), SR 5.2 RE(3), SR 6.1, SR 6.1 RE(1), SR 6.2, SR 7.1,SR 7.1 RE(1), SR 7.1 RE(2), SR 7.6
CONNECTIVITY | Does the asset have wireless capability? | Consider WiFi, Bluetooth, cellular, or other wireless technologies | SR 1.6, SR 1.6 RE(1), SR 2.2, SR 2.2 RE(1), SR 2.3, SR 2.3 RE(1), SR 4.3, SR 6.2, SR 7.6, SR 7.6 RE(1)
CONNECTIVITY | Does the asset require remote access? | Consider maintenance, monitoring, or operational access from outside the local network | SR 1.1, SR 1.1 RE(1), SR 1.1 RE(2), SR 1.1 RE(3), SR 1.3, SR 1.3 RE(1), SR 1.4, SR 1.5, SR 1.5 RE(1), SR 1.7, SR 1.7 RE(1), SR 1.8, SR 1.9, SR 1.9 RE(1), SR 1.11, SR 1.13, SR 1.13 RE(1), SR 2.1, SR 2.1 RE(1), SR 2.1 RE(2), SR 2.1 RE(3), SR 2.3,SR 2.3 RE(1), SR 2.6, SR 2.7, SR 2.12, SR 2.12 RE(1), SR 3.1, SR 3.1 RE(1), SR 3.5, SR 3.8,SR 3.8 RE(1), SR 3.8 RE(2), SR 3.8 RE(3), SR 4.3, SR 6.1, SR 6.1 RE(1), SR 6.2, SR 7.7
USER INTERACTION | Does the asset have user interfaces? | Consider HMIs, web interfaces, or command-line interfaces | SR 1.1, SR 1.1 RE(1), SR 1.1 RE(2), SR 1.1 RE(3), SR 1.3, SR 1.3 RE(1), SR 1.4, SR 1.5, SR 1.5 RE(1), SR 1.7, SR 1.7 RE(1), SR 1.7 RE(2), SR 1.10, SR 1.11, SR 1.12, SR 2.1, SR 2.1 RE(1), SR 2.1 RE(2), SR 2.1 RE(3), SR 2.5, SR 2.7, SR 2.12, SR 2.12 RE(1), SR 3.5, SR 3.8, SR 3.8 RE(1), SR 3.8 RE(2), SR 3.8 RE(3), SR 6.1, SR 6.1 RE(1)
PROGRAMMABILITY | Is the asset programmable? | Consider configuration changes, logic updates, or software modifications | SR 1.2, SR 1.2 RE(1), SR 2.1, SR 2.1 RE(1), SR 2.1 RE(2), SR 2.1 RE(3), SR 2.1 RE(4), SR 2.4, SR 2.4 RE(1), SR 2.10, SR 2.11, SR 2.11 RE(1), SR 2.11 RE(2), SR 3.3, SR 3.3 RE(1), SR 3.3 RE(2), SR 3.5, SR 3.6, SR 3.7, SR 7.3, SR 7.3 RE(1), SR 7.3 RE(2), SR 7.4, SR 7.7
PROGRAMMABILITY | Does the asset receive firmware updates? | Consider any form of software or firmware that can be updated | SR 3.4, SR 3.4 RE(1), SR 5.3, SR 5.3 RE(1), SR 7.3, SR 7.3 RE(1), SR 7.3 RE(2)
DATA HANDLING | Does the asset store data? | Consider configuration data, logs, or operational data | SR 2.10, SR 2.11, SR 2.11 RE(1), SR 2.11 RE(2), SR 3.9, SR 3.9 RE(1), SR 4.1, SR 4.1 RE(1), SR 4.1 RE(2), SR 4.2, SR 4.2 RE(1), SR 4.3, SR 7.3, SR 7.3 RE(1), SR 7.3 RE(2)
SAFETY CRITICALITY | Is the asset safety-critical? | Consider assets that could impact safety if compromised | SR 3.3, SR 3.3 RE(1), SR 3.3 RE(2), SR 3.6, SR 3.7, SR 5.3, SR 5.3 RE(1), SR 5.4, SR 7.4, SR 7.5
OPERATING SYSTEM | Does the asset have an operating system? | Consider traditional OS or embedded OS | SR 2.8, SR 2.8 RE(1), SR 2.9, SR 2.9 RE(1), SR 3.2, SR 3.2 RE(1), SR 3.2 RE(2), SR 3.4, SR 3.4 RE(1), SR 7.2
ALL ASSETS | All assets require inventory management | Applies to all assets regardless of characteristics | SR 7.8
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to Capture everything accurately (SR) Reply: Pull detailed SR () from Security Requirements sheet

## Threat Scenarios
Asset ID | Asset Name | Zone | Attack Vector | MITRE Technique | Attack Path Description | Safety Impact | Operational Impact | Worst Case Impact Rating | Risk Level
DOW_04 | Site Radio DMR | Communications Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits DMR management interface vulnerability. Gains control of site radio communications. Can manipulate or disrupt emergency channels including maintenance coordination. | 3 | 3 | 3 | Medium
DOW_04 | Site Radio DMR | Communications Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises radio system administrator credentials. Attacker gains full communications control through management interface. Can affect all channels and user groups. | 3 | 3 | 3 | Medium
DOW_04 | Site Radio DMR | Communications Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Radio system vendor compromise enables malicious update deployment. Backdoor installed through trusted channel. Ongoing communications control achieved. All radio functions potentially affected. | 3 | 3 | 3 | Medium
DOW_04 | Site Radio DMR | Communications Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses radio system controls. Uses maintenance access to disrupt communications. Can affect all channels including emergency and maintenance coordination. | 3 | 3 | 3 | Medium
DOW_06 | Perimeter Intrusion Detection | Security Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attacker exploits PIDS management system. Gains control of perimeter security monitoring. Can manipulate intrusion detection and suppress alerts. Integration with CCTV affected. | 4 | 3 | 4 | High
DOW_06 | Perimeter Intrusion Detection | Security Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises PIDS administrator credentials. Attacker gains full system control through management interface. Can modify all detection zones. | 4 | 3 | 4 | High
DOW_06 | Perimeter Intrusion Detection | Security Zone | Supply Chain | T0862/T0857: Supply Chain/Update | PIDS vendor compromise enables malicious update deployment. Backdoor installed through trusted channel. Ongoing system access achieved. All zones affected. | 4 | 3 | 4 | High
DOW_06 | Perimeter Intrusion Detection | Security Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses PIDS controls. Uses maintenance rights to modify detection parameters. Can create detection blind spots facility-wide. | 4 | 3 | 4 | High
DOW_08 | Intercommunications System | Communications Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits intercom management system vulnerability. Gains control of communication functions. Can affect gatehouse-facility coordination. | 3 | 2 | 3 | Medium
DOW_08 | Intercommunications System | Communications Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises intercom system credentials. Attacker gains full communication control. Can manipulate all intercom functions. | 3 | 2 | 3 | Medium
DOW_08 | Intercommunications System | Communications Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Intercom vendor compromise enables malicious update. Backdoor provides ongoing system access. All communication functions affected. | 3 | 2 | 3 | Medium
DOW_08 | Intercommunications System | Communications Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses intercom controls. Uses maintenance access to disrupt communications. Maximum system impact possible. | 3 | 2 | 3 | Medium
DOW_09 | EACAS | Security Zone | Remote Access | T0883/T0846: Remote Services/Discovery | Remote attack compromises access control interface. Gains control of facility access systems. Can modify permissions and alerts. | 4 | 3 | 4 | High
DOW_09 | EACAS | Security Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing of security staff. Harvests access control credentials. Attacker gains admin rights to security systems. | 4 | 3 | 4 | High
DOW_09 | EACAS | Security Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Security vendor compromise enables malicious update. Backdoor provides ongoing access control system access. Full permission control possible. | 4 | 3 | 4 | High
DOW_09 | EACAS | Security Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly manipulates access control systems. Uses admin rights to modify security configurations. Complete control of facility access. | 4 | 3 | 4 | High
DOW_10 | UPS Systems | Power Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits UPS management interface vulnerability. Gains access to backup power controls. Critical system manipulation achieved. | 4 | 3 | 4 | High
DOW_10 | UPS Systems | Power Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Phishing campaign targets facility staff. Compromises UPS system credentials. Attacker gains backup power control access. | 4 | 3 | 4 | High
DOW_10 | UPS Systems | Power Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | UPS vendor compromise enables malicious update deployment. Backdoor provides ongoing system access. Power backup manipulation possible. | 4 | 3 | 4 | High
DOW_10 | UPS Systems | Power Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses UPS controls. Uses maintenance rights to manipulate backup power. Maximum system impact achieved. | 4 | 3 | 4 | High
DOW_20 | Lighting Control | Building Systems Zone | Remote Access | T0883/T0879: Remote Services/Control | Attacker exploits DALI lighting control interface through vulnerable web ports. Gains direct access to lighting management system. Can manipulate all lighting zones including emergency paths and perimeter security lighting. | 3 | 2 | 3 | Medium
DOW_20 | Lighting Control | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing campaign compromises lighting system administrator credentials. Malicious attachment exploits PDF vulnerability. Attacker gains full lighting control through legitimate management interface. | 3 | 2 | 3 | Medium
DOW_20 | Lighting Control | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Compromised lighting control vendor pushes malicious system update. Backdoor installed through trusted update process. Attacker gains persistent lighting system access. | 3 | 2 | 3 | Medium
DOW_20 | Lighting Control | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider with maintenance access directly connects to lighting control system. Uses legitimate credentials to modify lighting configurations and override automation. | 3 | 2 | 3 | Medium
DOW_21 | Emergency Lighting | Safety Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attacker compromises emergency lighting monitoring system through exposed management port. Gains control of testing and monitoring functions. Can manipulate emergency lighting status and alerts. | 4 | 3 | 4 | High
DOW_21 | Emergency Lighting | Safety Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Phishing attack targets maintenance staff with spoofed system alert. Compromises emergency lighting system credentials. Attacker gains full administrative access. | 4 | 3 | 4 | High
DOW_21 | Emergency Lighting | Safety Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Vendor compromise enables malicious emergency lighting system update. Backdoor provides ongoing system access. Full control of monitoring and testing functions. | 4 | 3 | 4 | High
DOW_21 | Emergency Lighting | Safety Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses emergency lighting controls. Uses maintenance rights to modify system configuration. Can affect all emergency lighting zones. | 4 | 3 | 4 | High
DOW_22 | Energy Management | Building Systems Zone | Remote Access | T0883/T0846: Remote Services/Discovery | Attacker exploits energy management system web interface. Gains access to power monitoring and control functions. Can manipulate facility power distribution. | 3 | 3 | 3 | Medium
DOW_22 | Energy Management | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises EMS administrator access. Attacker gains control through legitimate management portal. Full power monitoring system access. | 3 | 3 | 3 | Medium
DOW_22 | Energy Management | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Energy management vendor compromise enables malicious update deployment. Backdoor installed through trusted channel. Ongoing system access achieved. | 3 | 3 | 3 | Medium
DOW_22 | Energy Management | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider connects directly to energy management system. Uses maintenance access to modify power configurations. Can affect facility-wide power distribution. | 3 | 3 | 3 | Medium
DOW_24 | BMS | IT/OT DMZ | Remote Access | T0886/T0846: Remote Services/Discovery | Attacker exploits BMS web interface vulnerability. Gains access to building control systems. Can manipulate critical environment parameters. | 4 | 3 | 4 | High
DOW_24 | BMS | IT/OT DMZ | Phishing | T0865/T0859: Spearphishing/Control | Phishing campaign targets facility staff. Compromises BMS admin credentials. Attacker gains building system control through VPN. | 4 | 3 | 4 | High
DOW_24 | BMS | IT/OT DMZ | Supply Chain | T0862/T0857: Supply Chain/Update | Vendor compromise enables malicious BMS update. Backdoor installed through trusted channel. Full building system control possible. | 4 | 3 | 4 | High
DOW_24 | BMS | IT/OT DMZ | Insider | T0884/T0831: Connection/Manipulation | Insider connects directly to BMS console. Uses maintenance access to modify system settings. Can affect all building controls. | 4 | 3 | 4 | High
DOW_25 | Fire Detection System | Safety Systems Zone | Remote Access | T0883/T0879: Remote Services/Inhibit Response Function | Attacker identifies exposed fire system management port through network scan. Exploits default credentials or known vulnerability in management interface. Gains direct access to fire detection configuration. Modifies detection thresholds and alert parameters. | 5 | 3 | 5 | Critical
DOW_25 | Fire Detection System | Safety Systems Zone | Phishing | T0865/T0867: Spearphishing/Command and Control | Targeted phishing attacks facility maintenance staff with spoofed fire system vendor alert. Malicious attachment compromises admin credentials. Attacker accesses system through legitimate admin portal with full configuration rights. | 5 | 3 | 5 | Critical
DOW_25 | Fire Detection System | Safety Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Software | Compromise of fire system vendor's update infrastructure. Malicious update pushed through legitimate channel. Backdoor installed with system-level privileges. Detection parameters can be remotely modified. | 5 | 3 | 5 | Critical
DOW_25 | Fire Detection System | Safety Systems Zone | Insider | T0884/T0831: Connection/Data Manipulation | Insider with system access directly connects to fire system controls. Uses maintenance credentials to modify configuration. Can disable sensors and suppress alerts facility-wide. | 5 | 3 | 5 | Critical
DOW_26 | Emergency Warning System | Safety Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | External attacker compromises emergency warning system remote access. Exploits management interface vulnerability. Gains control of facility-wide alert system. | 5 | 3 | 5 | Critical
DOW_26 | Emergency Warning System | Safety Systems Zone | Phishing | T0865/T0859: Spearphishing/Command | Targeted phishing of system administrators. Harvests emergency system credentials. Attacker gains full alert system control through admin portal. | 5 | 3 | 5 | Critical
DOW_26 | Emergency Warning System | Safety Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Compromised vendor pushes malicious warning system update. Backdoor provides remote system access. All alert functions can be controlled. | 5 | 3 | 5 | Critical
DOW_26 | Emergency Warning System | Safety Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses warning system controls. Uses maintenance rights to modify alert configurations. Can disable or manipulate all notifications. | 5 | 3 | 5 | Critical
DOW_27 | HVAC | Building Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attack compromises HVAC control through BMS interface. Gains access to temperature control systems. Can manipulate critical area cooling. | 3 | 2 | 3 | Medium
DOW_27 | HVAC | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Phishing campaign targets facility staff. Compromises HVAC system credentials. Attacker gains temperature control access through admin interface. | 3 | 2 | 3 | Medium
DOW_27 | HVAC | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | HVAC vendor compromise enables malicious system update. Backdoor provides ongoing temperature control access. Full system manipulation possible. | 3 | 2 | 3 | Medium
DOW_27 | HVAC | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly manipulates HVAC controls. Uses maintenance access to modify temperature settings. Can affect all facility cooling zones. | 3 | 2 | 3 | Medium
DOW_28 | CRAC | Building Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits CRAC system remote access. Gains control of critical area cooling. Can manipulate server room environment. | 4 | 3 | 4 | High
DOW_28 | CRAC | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises CRAC system credentials. Attacker gains environmental control through admin portal. Full cooling system access. | 4 | 3 | 4 | High
DOW_28 | CRAC | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Compromised vendor pushes malicious CRAC update. Backdoor enables ongoing system access. Temperature control manipulation possible. | 4 | 3 | 4 | High
DOW_28 | CRAC | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses CRAC controls. Uses maintenance rights to modify cooling parameters. Can affect critical equipment environment. | 4 | 3 | 4 | High
DOW_29 | PV Solar | Power Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attacker compromises solar system controls. Gains access to power generation management. Can affect supplementary power. | 3 | 2 | 3 | Medium
DOW_29 | PV Solar | Power Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises solar system credentials. Attacker gains generation control through admin interface. Full system access. | 3 | 2 | 3 | Medium
DOW_29 | PV Solar | Power Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Solar system vendor compromise enables malicious update. Backdoor provides ongoing access. Generation control manipulation possible. | 3 | 2 | 3 | Medium
DOW_29 | PV Solar | Power Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses solar controls. Uses maintenance rights to affect power generation. Maximum system impact achieved. | 3 | 2 | 3 | Medium
DOW_32 | OHLE SCADA | OT Zone | Remote Access | T0883/T0885: Commonly Used Port/Remote Services | Advanced attacker exploits vulnerable HTTP/HTTPS ports (80/443) on engineering workstation remote interface. Gains initial foothold by exploiting unpatched vulnerability in remote access service. Pivots through engineering workstation to access SCADA control network. Establishes persistent backdoor through firewall using standard allowed ports. | 5 | 4 | 5 | Critical
DOW_32 | OHLE SCADA | OT Zone | Phishing | T0865/T0866: Spearphishing/Exploitation for Credential Access | Sophisticated phishing campaign targets maintenance engineers with convincing vendor security update notification. Malicious PDF attachment exploits zero-day vulnerability in PDF reader. Harvests cached VPN credentials and remote desktop session tokens. Establishes persistent access through legitimate maintenance channels. | 5 | 4 | 5 | Critical
DOW_32 | OHLE SCADA | OT Zone | Supply Chain | T0862/T0857: Supply Chain Compromise/Command and Control | Threat actor compromises SCADA vendor's software update infrastructure. Injects malicious code into legitimate system updates. Malware deployed through trusted update channel with elevated system privileges. Establishes persistent backdoor through modified system libraries. | 5 | 4 | 5 | Critical
DOW_32 | OHLE SCADA | OT Zone | Insider | T0822/T0831: External Remote Services/Data Manipulation | Malicious insider with maintenance access and detailed system knowledge directly connects to SCADA console. Uses legitimate credentials to access engineering workstation. Modifies system configurations and safety parameters. Plants persistent remote access backdoor. | 5 | 4 | 5 | Critical
DOW_33 | PA System | Building Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits PA system management interface vulnerability. Gains direct access to announcement controls. Can broadcast unauthorized messages facility-wide. | 3 | 2 | 3 | Medium
DOW_33 | PA System | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises PA system administrator credentials. Attacker gains full broadcast control through management portal. Can manipulate all announcements. | 3 | 2 | 3 | Medium
DOW_33 | PA System | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | PA system vendor compromise enables malicious update deployment. Backdoor installed through trusted channel. Ongoing announcement control achieved. | 3 | 2 | 3 | Medium
DOW_33 | PA System | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses PA controls. Uses maintenance rights to broadcast unauthorized messages. Can affect all facility communications. | 3 | 2 | 3 | Medium
DOW_34 | Backup Generator | Power Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attacker compromises generator control system. Gains access to backup power management. Can manipulate emergency power availability. | 4 | 3 | 4 | High
DOW_34 | Backup Generator | Power Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Phishing campaign targets maintenance staff. Compromises generator system credentials. Attacker gains emergency power control. | 4 | 3 | 4 | High
DOW_34 | Backup Generator | Power Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Generator control system vendor compromised. Malicious update deployed through trusted channel. Backdoor enables ongoing system access. | 4 | 3 | 4 | High
DOW_34 | Backup Generator | Power Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly manipulates generator controls. Uses maintenance access to affect backup power availability. Maximum system impact. | 4 | 3 | 4 | High
DOW_36 | Air Compressor | Building Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Attacker exploits compressor control interface. Gains access to compressed air systems. Can manipulate industrial process support. | 3 | 2 | 3 | Medium
DOW_36 | Air Compressor | Building Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises compressor system credentials. Attacker gains control through management interface. Full system access achieved. | 3 | 2 | 3 | Medium
DOW_36 | Air Compressor | Building Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Compressor vendor compromise enables malicious update. Backdoor provides ongoing system access. Process support manipulation possible. | 3 | 2 | 3 | Medium
DOW_36 | Air Compressor | Building Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly accesses compressor controls. Uses maintenance rights to manipulate air systems. Maximum operational impact possible. | 3 | 2 | 3 | Medium
DOW_38 | HV Transformers | Power Systems Zone | Remote Access | T0883/T0879: Remote Services/Function | Remote attack compromises transformer control system. Gains access to high voltage power distribution. Critical system manipulation possible. | 5 | 4 | 5 | Critical
DOW_38 | HV Transformers | Power Systems Zone | Phishing | T0865/T0859: Spearphishing/Control | Targeted phishing compromises power system credentials. Attacker gains transformer control through admin interface. Full system access. | 5 | 4 | 5 | Critical
DOW_38 | HV Transformers | Power Systems Zone | Supply Chain | T0862/T0857: Supply Chain/Update | Power system vendor compromise enables malicious update deployment. Backdoor installed through trusted channel. Ongoing control access. | 5 | 4 | 5 | Critical
DOW_38 | HV Transformers | Power Systems Zone | Insider | T0884/T0831: Connection/Manipulation | Insider directly manipulates transformer controls. Uses maintenance access to affect power distribution. Maximum system impact possible. | 5 | 4 | 5 | Critical
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:
:

## Security Requirements
SR ID | FR | SL | Title | Description | Railway Notes | Relevant Design Principles | Stakeholder | Type | Min SL | Relevant Asset Characteristics | MITRE TTPs Addressed | IEC62443-3-3 Requirement
SR 1.1 | FR 1 - Identification and authentication control (IAC) | 1 | Human user identification and authentication | The control system shall provide the capability to identify and authenticate all human users. This capability shall enforce such identification and authentication on all interfaces which provide human user access to the control system to support segregation of duties and least privilege in accordance with applicable security policies and procedures. | This includes application interfaces such as web server, file transfer protocol (FTP) server, OPC, and remote desktop interfaces that provide network access to human users and that do not securely convey the authenticated IACS user identity to the application during connection. It is acceptable to implement this requirement in combination with other external authentication solutions including physical security measures in railways. | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 1 | User Interfaces, Remote Access | T0859, T0812, T0891 | 5.3
SR 1.1 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | Unique identification and authentication | The control system shall provide the capability to uniquely identify and authenticate all human users. |  | 6 - Authenticate requests, 13 - Precautionary principle | Sys, Sup | Tech | 2 | User Interfaces, Remote Access | T0859, T0812, T0891 | 5.3.3.1
SR 1.1 RE(2) | FR 1 - Identification and authentication control (IAC) | 3 | Multifactor authentication for untrusted networks | The control system shall provide the capability to employ multifactor authentication for human user access to the control system via an untrusted network (See 5.15, SR 1.13 - Access via untrusted networks). | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities. | 6 - Authenticate requests, 12 - Proportionality principle | Sys, Sup | Tech | 3 | User Interfaces, Remote Access, TCP/IP Network | T0859, T0812, T0891 | 5.3.3.2
SR 1.1 RE(3) | FR 1 - Identification and authentication control (IAC) | 4 | Multifactor authentication for all networks | The control system shall provide the capability to employ multifactor authentication for all human user access to the control system. | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities. | 6 - Authenticate requests, 12 - Proportionality principle | Op, Sys | Tech | 4 | User Interfaces, Remote Access | T0859, T0812, T0891 | 5.3.3.3
SR 1.2 | FR 1 - Identification and authentication control (IAC) | 2 | Identification and authentication of software processes and devices | The control system shall provide the capability to identify and authenticate all software processes and devices. This capability shall enforce such identification and authentication on all interfaces which provide access to the control system to support least privilege in accordance with applicable security policies and procedures. | Note that in the equivalent requirement IEC 62443-2-1 / IEC 62443-2-4 USER-07 "sw services are considered instead of "sw processes": USER-07: All software services shall be identified and authenticated prior to their execution. Identification of internal software processes/services and devices are not a common practice in railway applications or railway systems. | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 2 | TCP/IP Network, Programmable | T0800, T0859, T0849 | 5.4
SR 1.2 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Unique identification and authentication of software processes and devices | The control system shall provide the capability to uniquely identify and authenticate all software processes and devices. |  | 6 - Authenticate requests, 12 - Proportionality principle, 13 - Precautionary principle | Sys, Sup | Tech | 3 | TCP/IP Network, Programmable | T0800, T0859, T0849 | 5.4.3.1
SR 1.3 | FR 1 - Identification and authentication control (IAC) | 1 | Account management | The control system shall provide the capability to support the management of all accounts by authorized users, including adding, activating, modifying, disabling and removing accounts. | Railways have mostly a distributed system supported by simple passwords. The full account management requires a major change in the existing control/command and IT infrastructure. The issue of maintenance and multiple commercial contractors complicates the issue. | 5 - Economize mechanism, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 1 | User Interfaces, Remote Access | T0859, T0812 | 5.5
SR 1.3 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Unified account management | The control system shall provide the capability to support unified account management. | The operators should install a unique account and user administration system in combination with physical security in fulfilment of this requirement. The decision for the appropriate solution is left to the operators ideally in a standardized manner across the railway industry. | 6 - Authenticate requests, 9 - Make security usable | Sys, Sup | Tech | 3 | User Interfaces, Remote Access | T0859, T0812 | 5.5.3.1
SR 1.4 | FR 1 - Identification and authentication control (IAC) | 1 | Identifier management | The control system shall provide the capability to support the management of identifiers by user, group, role or control system interface. | An Identifier is a construct (username, tag) which is associated closely to a user or subscriber. Authentication is a procedure based on a secret given by an identified user or subscriber which enable the verification of it, maybe uniquely. There are currently no solutions for railway environments for this requirement as an inherent system solution. Railways have mostly a distributed system supported by simple passwords. Full account management can often only support with an external solution in a form of compensating countermeasures. | 6 - Authenticate requests, 9 - Make security usable | Sys, Sup | Tech | 1 | User Interfaces, Remote Access | T0859, T0891 | 5.6
SR 1.5 | FR 1 - Identification and authentication control (IAC) | 1 | Authenticator management | The control system shall provide the capability to: a) initialize authenticator content; b) change all default authenticators upon control system installation; c) change/refresh all authenticators; and d) protect all authenticators from unauthorized disclosure and modification when stored and transmitted. | In case a unique authentication management system for the railway system is not feasible, an external solution based on compensating countermeasures should be considered. | 6 - Authenticate requests, 8 - Assume secrets not safe, 9 - Make security usable | Op, Sys, Sup | Tech, Proc | 1 | User Interfaces, Remote Access | T0812, T0891 | 5.7
SR 1.5 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Hardware security for software process identity credentials | For software process and device users | the control system shall provide the capability to protect the relevant authenticators via hardware mechanisms. | Credentials used as a base of trust shall be storage with Hardware Secure Mechanism. If this for meaningful reasons is not possible the chain of trust should be supported by logically Secure Mechanism plus a compensating countermeasure (e.g. monitoring). | 8 - Assume secrets not safe | Sys, Sup | Tech | 3 | User Interfaces, Remote Access, Programmable | T0812, T0891 | 5.7.3.1
SR 1.6 | FR 1 - Identification and authentication control (IAC) | 1 | Wireless access management | The control system shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. | - | 1 - Secure the weakest link, 6 - Authenticate requests, 7 - Control access, 12 - Proportionality principle | Op, Sys, Sup | Tech, Proc | 1 | Wireless Capability | T0860, T0887 | 5.8
SR 1.6 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | Unique identification and authentication | The control system shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication. | - | 1 - Secure the weakest link, 6 - Authenticate requests, 12 - Proportionality principle | Sys, Sup | Tech | 2 | Wireless Capability | T0860, T0887 | 5.8.3.1
SR 1.7 | FR 1 - Identification and authentication control (IAC) | 1 | Strength of password-based authentication | For control systems utilizing password-based authentication, the control system shall provide the capability to enforce configurable password strength based on minimum length and variety of character types. | This will be a big challenge especially for the maintainers. They are used to very simple passwords today and to non-personal (role specific) login. But SR 1.7 is a must because most components cannot be protected against brute force login attempts. In case this requirement cannot be fulfilled the integrity of authentication information should be supported by external means and compensating countermeasures (e.g. use of personal card readers to control access to restricted areas and functions) | 8 - Assume secrets not safe, 9 - Make security usable, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 1 | User Interfaces, Remote Access | T0812, T0891 | 5.9
SR 1.7 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Password generation and lifetime restrictions for human users | The control system shall provide the capability to prevent any given human user account from reusing a password for a configurable number of generations. In addition, the control system shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform with commonly accepted security industry practices. | Lifetime restriction for human users is not currently consistently implemented in railways. To support this, an external solution with additional system capability can be used e.g. for authentication control as a compensating countermeasure. | 8 - Assume secrets not safe, 9 - Make security usable | Sup | Tech | 3 | User Interfaces, Remote Access | T0812, T0891 | 5.9.3.1
SR 1.7 RE(2) | FR 1 - Identification and authentication control (IAC) | 4 | Password lifetime restrictions for all users | The control system shall provide the capability to enforce password minimum and maximum lifetime restrictions for all users. | In addition, the railway application should enforce password minimum and maximum lifetime restrictions for human user | 6 - Authenticate requests, 8 - Assume secrets not safe, 9 - Make security usable | Op, Sup | Proc, Tech | 4 | User Interfaces, Remote Access | T0812, T0891 | 5.9.3.2
SR 1.8 | FR 1 - Identification and authentication control (IAC) | 2 | Public Key Infrastructure (PKI) Certificates | Where PKI is utilized, the control system shall provide the capability to operate a PKI according to commonly accepted best practices or obtain public key certificates from an existing PKI. | - | 8 - Assume secrets not safe, 9 - Make security usable | Op, Sup | Proc, Tech | 2 | TCP/IP Network, Remote Access | T0849 | 5.1
SR 1.9 | FR 1 - Identification and authentication control (IAC) | 2 | Strength of public key authentication | For control system utilizing public key authentication, the control system shall provide the capability to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate certificates by constructing a certification path to an accepted CA or in the case of self-signed certificates by deploying leaf certificates to all hosts with communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate's revocation status; d) establish user (human, software process or device) control of the corresponding private key; and e) map the authenticated identity to a user (human, softare process or device). | In case the given requirements for validation of certificates cannot be supported in railway system, an external solution (e.g. an offline copy of the CA that is updated every 24 h) as compensating countermeasure should be established. | 6 - Authenticate requests, 8 - Assume secrets not safe, 9 - Make security usable | Op, Sys, Sup | Tech, Proc | 3 | TCP/IP Network, Remote Access | T0859, T0849 | 5.11
SR 1.9 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Hardware security for public key authentication | The control system shall provide the capability to protect the relevant private keys via hardware mechanisms according to commonly accepted security industry practices practices and recommendations. | - | 8 - Assume secrets not safe, 9 - Make security usable | Sup | Tech | 3 | TCP/IP Network, Remote Access | T0859, T0849 | 5.11.3.1
SR 1.10 | FR 1 - Identification and authentication control (IAC) | 1 | Authenticator feedback | The control system shall provide the capability to obscure feedback of authentication information during the authentication process. | - | 8 - Assume secrets not safe, 9 - Make security usable | Sys | Tech | 1 | User Interfaces, Remote Access | T0812, T0891 | 5.12
SR 1.11 | FR 1 - Identification and authentication control (IAC) | 1 | Unsuccessful login attempts | The control system shall provide the capability to enforce a limit of a configurable number of consecutive invalid access attempts by any user (human, software process or device) during a configurable time period. The control system shall provide the capability to deny access for a specified period of time or until unlocked by an administrator when this limit has been exceeded. For system accounts on behalf of which critical services or servers are run, the control system shall provide the capability to disallow interactive logons. | For mission or safety critical systems that deliver essential railway functions, limitation on login attempts may result in system or function unavailability and adversely affect safety. Implementation of this requirement should be fully cognisant of safety and operational availability implications. For example, a freezing of a system (e.g. safe stop in an ETCS Level 2 system) can lead to an unsafe situation. Thus, the required system reaction shall be defined with respect to safety and availability. | 6 - Authenticate requests, 7 - Control access, 9 - Make security usable | Op, Sys, Sup | Tech | 1 | User Interfaces, Remote Access | T0859, T0812 | 5.13
SR 1.12 | FR 1 - Identification and authentication control (IAC) | 1 | System use notification | The control system shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized personnel. | - | 6 - Authenticate requests, 9 - Make security usable, 10 - Promote privacy | Sys, Sup | Tech | 1 | User Interfaces, Remote Access | T0859, T0891 | 5.14
SR 1.13 | FR 1 - Identification and authentication control (IAC) | 1 | Access via untrusted networks | The control system shall provide the capability to monitor and control all methods of access to the control system via untrusted networks. | - | 11 - Audit and monitor | Op, Sys, Sup | Proc, Tech | 1 | TCP/IP Network, Remote Access | T0865, T0822, T0860 | 5.15
SR 1.13 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | Explicit access request approval | The control system shall provide the capability to deny access requests via untrusted networks unless approved by an assigned role. | - | 6 - Authenticate requests, 13 - Precautionary principle | Op, Sys, Sup | Proc, Tech | 2 | TCP/IP Network, Remote Access | T0865, T0822, T0860 | 5.15.3.1
SR 2.1 | FR 2 - Use control (UC) | 1 | Authorization enforcement | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all human users for controlling use of the control system to support segregation of duties and least privilege. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 1 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | 6.3
SR 2.1 RE(1) | FR 2 - Use control (UC) | 2 | Authorization enforcement for all users | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all users (humans, software processes and devices) for controlling use of the control system to support segregation of duties and least privilege. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 2 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | 6.3.3.1
SR 2.1 RE(2) | FR 2 - Use control (UC) | 2 | Permission mapping to roles | The control system shall provide the capability for an authorized user or role to define and modify the mapping of permissions to roles for all human users. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 2 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | 6.3.3.2
SR 2.1 RE(3) | FR 2 - Use control (UC) | 3 | Supervisor override | The control system shall support supervisor manual override of the current human user authorizations for a configurable time or event sequence. | Railway operators do not generally have a supervisor to oversee the integrity of their actions and decisions. There is always one person fully responsible for a task (e.g. cab driver for his train running). Supervisor override is common in railways in order to manually accept special situations. These are documented in a juridical way. | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 3 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | 6.3.3.3
SR 2.1 RE(4) | FR 2 - Use control (UC) | 4 | Dual approval | The control system shall support dual approval where an action can result in serious impact on the industrial process. | This may conflict with time critical activities/functions. In case of such conflicts, this requirement should be implemented with alternative approaches to establish the chain of trust efficiently. For example, changing a set point in the TCMS that can affect the computation of the speed of the train should require a dual approval; bypassing the ETCS control of the speed of the train may require a pre-defined sequence of actions, carefully chosen to minimize the risk of accidental execution, performed by the driver in case of danger. | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 4 | User Interfaces, Remote Access, Programmable, Safety Critical | T0800, T0859, T0863 | 6.3.3.4
SR 2.2 | FR 2 - Use control (UC) | 1 | Wireless use control | The control system shall provide the capability to authorize, monitor and enforce usage restrictions for wireless connectivity to the control system according to commonly accepted security industry practices. | - | 5 - Economize mechanism, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech | 1 | Wireless Capability | T0860, T0887 | 6.4
SR 2.2 RE(1) | FR 2 - Use control (UC) | 3 | Identify and report unauthorized wireless devices | The control system shall provide the capability to identify and report unauthorized wireless devices transmitting within the control system physical environment. | - | 7 - Control Access | Op, Sys, Sup | Tech | 3 | Wireless Capability | T0860, T0887 | 6.4.3.1
SR 2.3 | FR 2 - Use control (UC) | 1 | Use control for portable and mobile devices | The control system shall provide the capability to automatically enforce configurable usage restrictions that include: a) preventing the use of portable and mobile devices; b) requiring context specific authorization; and c) restricting code and data transfer to/from portable and mobile devices. | Portable and mobile devices are already widely used in railway infrastructure. E.g. for diagnostic purposes but also to safety relevant purposes such as shunting / track works. A secure management of mobile access is crucial in the safety critical railway environment. | 6 - Authenticate requests, 7 - Control access, 16 - Secure Defaults | Op, Sys | Tech, Proc | 1 | Remote Access, Wireless Capability | T0864, T0860 | 6.5
SR 2.3 RE(1) | FR 2 - Use control (UC) | 3 | Enforcement of security status of portable and mobile devices | The control system shall provide the capability to verify that portable or mobile devices attempting to connect to a zone comply with the security requirements of that zone. | - | 7 - Control access, 16 - Secure Defaults | Op, Sys | Tech | 3 | Remote Access, Wireless Capability | T0864, T0860 | 6.5.3.1
SR 2.4 | FR 2 - Use control (UC) | 1 | Mobile code | The control system shall provide the capability to enforce usage restrictions for mobile code technologies based on the potential to cause damage to the control system that include: a) preventing the execution of mobile code; b) requiring proper authentication and authorization for origin of the code; c) restricting mobile code transfer to/from the control system; and d) monitoring the use of mobile code. | - | 6 - Authenticate requests, 7 - Control access, 16 - Secure Defaults | Sys, Sup | Tech | 2 | Programmable, TCP/IP Network | T0865, T0873 | 6.6
SR 2.4 RE(1) | FR 2 - Use control (UC) | 3 | Mobile code integrity check | The control system shall provide the capability to verify integrity of the mobile code before allowing code execution. | - | 7 - Control access, 8 - Assume secrets not safe | Sys, Sup | Tech | 3 | Programmable, TCP/IP Network | T0865, T0873 | 6.6.3.1
SR 2.5 | FR 2 - Use control (UC) | 1 | Session lock | The control system shall provide the capability to prevent further access by initiating a session lock after a configurable time period of inactivity or by manual initiation. The session lock shall remain in effect until the human user who owns the session or another authorized human user re-establishes access using appropriate identification and authentication procedures. | In view of the safety critical nature of the railway environment, session locks should be carefully applied so as not to interact adversely with system availability and access to essential functions. For example, the user screen could be locked upon user request or after a configured period of inactivity and require re-authentication if an authorized user wants to unlock it. | 5 - Economize mechanism, 7 - Control access | Op, Sys, Sup | Tech | 2 | User Interfaces | T0882, T0863 | 6.7
SR 2.6 | FR 2 - Use control (UC) | 2 | Remote session termination | The control system shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity or manually by the user who initiated the session. | - | 5 - Economize mechanism, 7 - Control access | Op, Sys, Sup | Tech | 2 | Remote Access | T0822, T0886 | 6.8
SR 2.7 | FR 2 - Use control (UC) | 3 | Concurrent session control | The control system shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device) to a configurable number of sessions. | - | 5 - Economize mechanism, 7 - Control access | Op, Sys, Sup | Tech, Proc | 3 | Remote Access, User Interfaces | T0882, T0859 | 6.9
SR 2.8 | FR 2 - Use control (UC) | 1 | Auditable events | The control system shall provide the capability to generate audit records relevant to security for the following categories: access control, request errors, operating system events, control system events, backup and restore events, configuration changes, potential reconnaissance activity and audit log events. Individual audit records shall include the timestamp, source (originating device, software process or human user account), category, type, event ID and event result. | - | 11 - Audit and monitor | Sys, Sup | Tech | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.1
SR 2.8 RE(1) | FR 2 - Use control (UC) | 3 | Centrally managed, system-wide audit trail | The control system shall provide the capability to centrally manage audit events and to compile audit records from multiple components throughout the control system into a system-wide (logical or physical), time-correlated audit trail. The control system shall provide the capability to export these audit records in industry standard formats for analysis by standards commercial log analysis tools, for example, security information and event management (SIEM). | Components and sub-systems that log events locally should ensure the monitoring and logging information are transferred to a centrally managed system. There may be a time delay between the local logging data and the transfer to the central system | 11 - Audit and monitor | Sys, Sup | Tech | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.10.3.1
SR 2.9 | FR 2 - Use control (UC) | 1 | Audit storage capacity | The control system shall allocate sufficient audit record storage capacity according to commonly recognized recommendations for log management and system configuration. The control system shall provide auditing mechanisms to reduce the likelihood of such capacity being exceeded. | - | 11 - Audit and monitor | Sys, Sup | Tech | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.11
SR 2.9 RE(1) | FR 2 - Use control (UC) | 3 | Warn when audit record storage capacity threshold reached | The control system shall provide the capability to issue a warning when the allocated audit record storage volume reaches a configurable percentage of maximum audit record storage capacity. | - | 11 - Audit and monitor | Sys, Sup | Tech | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.11.3.1
SR 2.10 | FR 2 - Use control (UC) | 1 | Response to audit processing failures | The control system shall provide the capability to alert personnel and prevent the loss of essential services and functions in the event of an audit procession failure. The control system shall provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations. | - | 11 - Audit and monitor | Op, Sys, Sup | Tech | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.12
SR 2.11 | FR 2 - Use control (UC) | 2 | Timestamps | The control system shall provide timestamps for use in audit record generation. | The time source should be protected from unauthorized alteration | 11 - Audit and monitor | Sys, Sup | Tech | 2 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.13
SR 2.11 RE(1) | FR 2 - Use control (UC) | 3 | Internal time synchronization | The control system shall provide the capability to synchronize internal system clocks at a configurable frequency. | - | 11 - Audit and monitor | Sys, Sup | Tech | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.13.3.1
SR 2.11 RE(2) | FR 2 - Use control (UC) | 4 | Protection of time source integrity | The time source shall be protected from unauthorized alteration and shall cause an audit event upon alteration. | - | 11 - Audit and monitor | Sys, Sup | Tech | 4 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | 6.13.3.2
SR 2.12 | FR 2 - Use control (UC) | 3 | Non-repudiation for human users | The control system shall provide the capability to determine whether a given human user took a particular action. | - | 6 - Authenticate requests | Op, Sys, Sup | Tech, Proc | 3 | User Interfaces, Data Storage | T0859, T0872, T0863 | 6.14
SR 2.12 RE(1) | FR 2 - Use control (UC) | 4 | Non-repudiation for all users | The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action. | - | 6 - Authenticate requests | Op, Sys, Sup | Tech, Proc | 4 | User Interfaces, Data Storage, TCP/IP Network | T0859, T0872, T0863 | 6.14.3.1
SR 3.1 | FR 3 - System integrity (SI) | 1 | Communication integrity | The control system shall provide the capability to protect the integrity of transmitted information. | - | 6 - Authenticate requests, 14 - Continuous protection | Sys, Sup | Tech | 1 | TCP/IP Network, Remote Access | T0800, T0842, T0887 | 7.3
SR 3.1 RE(1) | FR 3 - System integrity (SI) | 3 | Cryptographic integrity protection | The control system shall provide the capability to employ cryptographic mechanisms to recognize changes to information during communication. | The cryptographic mechanisms employed should be secure. Rolling stock and restricted network segments with an adequate boundary, intrusion detection and diverse transmission channel (e.g. use of Ethernet and MVB) can use these as compensating countermeasures. Open untrusted networks without compensating countermeasures require this extra protection in railways. | 14 - Continuous protection | Sys, Sup | Tech | 3 | TCP/IP Network, Remote Access | T0800, T0842, T0887 | 7.3.3.1
SR 3.2 | FR 3 - System integrity (SI) | 1 | Malicious code protection | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms. | Prevention means mechanisms such as removable media control, and workstation and laptop management policies, used in conjunction with means of detection at railway system entry points (e.g. USB cleaning stations, IDS, etc.) may be preferred as a compensating security measure from detection mechanisms deployed on all railway embedded devices. Use of USB ports should be strictly limited. When no other solution is available, USB controller and OS driver hardening should be employed to prevent execution of code from USB devices. A secure boot mechanism and a white list application management at operating system/firmware and application layers is required to ensure only authorized software is permitted and executed. | 1 - Secure the weakest link, 2 - Defence-in-depth, 11 - Audit and monitor, 14 - Continuous Protection, 17 - Trusted Components | Op, Sys, Sup | Tech, Proc | 1 | TCP/IP Network, Operating System | T0873, T0865 | 7.4
SR 3.2 RE(1) | FR 3 - System integrity (SI) | 2 | Malicious code protection on entry and exit points | The control system shall provide the capability to employ malicious code protection mechanisms at all entry and exit points. | This RE should be managed at SL1 level to be consistent with SR 3.2 in railways | 7 - Control Access, 12 - Proportionality principle | Op, Sys, Sup | Tech, Proc, Env | 2 | TCP/IP Network, Operating System | T0873, T0865 | 7.4.3.1
SR 3.2 RE(2) | FR 3 - System integrity (SI) | 3 | Central management and reporting for malicious code protection | The control system shall provide the capability to manage malicious code protection mechanisms. | Malware and malicious code protection should be centrally managed for integrity and consistency in railways. SIEM protection is largely a dynamic anomaly detection/protection mechanism and may prove inadequate for malicious code protection. | 9 - Make security usable | Op, Sys | Tech, Proc | 3 | TCP/IP Network, Operating System | T0873, T0865 | 7.4.3.2
SR 3.3 | FR 3 - System integrity (SI) | 1 | Security functionality verification | The control system shall provide the capability to support verification of the intended operation of security functions and report when anomalies are discovered during FAT, SAT and scheduled maintenance. These security functions shall include all those necessary to support the security requirements specified in this standard. | - | 3 - Fail secure, 11 - Audit and monitor | Sys, Sup | Tech | 2 | Safety Critical, Programmable | T0889, T0821, T0838 | 7.5
SR 3.3 RE(1) | FR 3 - System integrity (SI) | 3 | Automated mechanisms for security functionality verification | The control system shall provide the capability to employ automated mechanisms to support management of security verification during FAT, SAT and scheduled maintenance. | - | 9 - Make security usable | Sys, Sup | Tech, Proc | 3 | Safety Critical, Programmable | T0889, T0821, T0838 | 7.5.3.1
SR 3.3 RE(2) | FR 3 - System integrity (SI) | 4 | Security functionality verification during normal operation | The control system shall provide the capability to support verification of the intended operation of security functions during normal operations. | This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems | 9 - Make security usable | Sys | Tech, Proc | 4 | Safety Critical, Programmable | T0889, T0821, T0838 | 7.5.3.2
SR 3.4 | FR 3 - System integrity (SI) | 2 | Software and information integrity | The control system shall provide the capability to detect, record, report and protect against unauthorized changes to software and information at rest. | - | 8 - Assume secrets not safe, 11 - Audit and monitor, 13 - Precautionary principle | Sys, Sup | Tech | 1 | Firmware Updates, Operating System | T0873, T0857, T0839 | 7.6
SR 3.4 RE(1) | FR 3 - System integrity (SI) | 3 | Automated notification about integrity violations | The control system shall provide the capability to use automated tools that provide notification to a configurable set of recipients upon discovering discrepancies during integrity verification. | - | 9 - Make security usable, 14 - Continuous Protection | Sup | Tech | 3 | Firmware Updates, Operating System | T0873, T0857, T0839 | 7.6.3.1
SR 3.5 | FR 3 - System integrity (SI) | 1 | Input validation | The control system shall validate the syntax and content of any input which is used as an industrial process control input or input that directly impacts the action of the control system. | - | 2 - Defence-indepth, 7 - Control Access, 14 - Continuous Protection | Sup | Tech | 2 | User Interfaces, Remote Access, Programmable | T0871, T0821 | 7.7
SR 3.6 | FR 3 - System integrity (SI) | 1 | Deterministic output | The control system shall provide the capability to set outputs to a predetermined state if normal operation cannot be maintained as a result of an attack. | - | 3 - Fail secure, 12 - Proportionality principle, 13 - Precautionary principle | Sys, Sup | Tech, Proc | 2 | Safety Critical, Programmable | T0821, T0838, T0836 | 7.8
SR 3.7 | FR 3 - System integrity (SI) | 2 | Error handling | The control system shall identify and handle error conditions in a manner such that effective remediation can occur. This shall be done in a manner which does not provide information that could be exploited by adversaries to attack the IACS unless revealing this information is necessary for the timely troubleshooting of problems. | - | 9 - Make security usable, 10 - Promote privacy, 11 - Audit and monitor | Sys, Sup | Tech, Proc | 2 | Safety Critical, Programmable | T0816, T0838 | 7.9
SR 3.8 | FR 3 - System integrity (SI) | 2 | Session integrity | The control system shall provide the capability to protect the integrity of sessions. The control system shall reject any usage of invalid session IDs. | - | 6 - Authenticate requests, 7 - Control Access | Sup | Tech | 2 | Remote Access, User Interfaces | T0882, T0822 | 7.1
SR 3.8 RE(1) | FR 3 - System integrity (SI) | 3 | Invalidation of session IDs after session termination | The control system shall provide the capability to invalidate session IDs upon user logout or other session termination (including browser sessions). | - | 9 - Make security usable | Sup | Tech, Op | 3 | Remote Access, User Interfaces | T0882, T0822 | 7.10.3.1
SR 3.8 RE(2) | FR 3 - System integrity (SI) | 3 | Unique session ID generation | The control system shall provide the capability to generate a unique session ID for each session and treat all unexpected session IDs as invalid. | - | 8 - Assume secrets not safe | Sup | Tech | 3 | Remote Access, User Interfaces | T0882, T0822 | 7.10.3.2
SR 3.8 RE(3) | FR 3 - System integrity (SI) | 4 | Randomness of session IDs | The control system shall provide the capability to generate unique session IDs with commonly accepted sources of randomness. | - | 8 - Assume secrets not safe | Sup | Tech | 4 | Remote Access, User Interfaces | T0882, T0822 | 7.10.3.3
SR 3.9 | FR 3 - System integrity (SI) | 2 | Protection of audit information | The control system shall protect audit information and audit tools (if present) from unauthorized access, modification and deletion. | - | 4 - Grant least privilege | Sys, Sup | Tech | 3 | Data Storage, TCP/IP Network | T0809, T0872 | 7.11
SR 3.9 RE(1) | FR 3 - System integrity (SI) | 4 | Audit records on write-once media | The control system shall provide the capability to produce audit records on hardware-enforced write-once media. | - | 13 - Precautionary principle | Sup | Tech | 4 | Data Storage, TCP/IP Network | T0809, T0872 | 7.11.3.1
SR 4.1 | FR 4 - Data confidentiality (DC) | 1 | Information confidentiality | The control system shall provide the capability to protect the confidentiality of information for which explicit read authorization is supported, whether at rest or in transit. | - | 4 - Grant least privilege, 8 - Assume secrets not safe, 15 - Secure Metadata Management, 16 - Secure Defaults | Sup, Sys | Tech | 1 | TCP/IP Network, Data Storage | T0882, T0842, T0887 | 8.3
SR 4.1 RE(1) | FR 4 - Data confidentiality (DC) | 2 | Protection of confidentiality at rest or in transit via untrusted networks | The control system shall provide the capability to protect the confidentiality of information at rest and remote access sessions traversing an untrusted network. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access, 8 - Assume secrets not safe, 10 - Promote privacy | Sys, Op | Tech, Proc | 2 | TCP/IP Network, Data Storage, Remote Access | T0882, T0842, T0887 | 8.3.3.1
SR 4.1 RE(2) | FR 4 - Data confidentiality (DC) | 4 | Protection of confidentiality across zone boundaries | The control system shall provide the capability to protect the confidentiality of information traversing any zone boundary. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access, 8 - Assume secrets not safe, 10 - Promote privacy | Sup, Sys | Tech, Proc | 4 | TCP/IP Network, Data Storage | T0882, T0842, T0887 | 8.3.3.2
SR 4.2 | FR 4 - Data confidentiality (DC) | 2 | Information persistence | The control system shall provide the capability to purge all information for which explicit read authorization is supported from components to be released from active service and/or decommissioned. | Current railway applications do not implement extensive permission management so implementation of this requirement for information purging in components and systems is challenging. Read authorization should not be the only criteria for data/information criticality that qualifies for purging. | 7 - Control access, 15 - Secure Metadata Management, 16 - Secure Defaults | Sup, Sys, Op | Tech, Proc | 2 | Data Storage | T0882, T0811 | 8.4
SR 4.2 RE(1) | FR 4 - Data confidentiality (DC) | 3 | Purging of shared memory resources | The control system shall provide the capability to prevent unauthorized and unintended information transfer via volatile shared memory resources. | - | 8 - Assume secrets not safe | Op | Tech | 3 | Data Storage | T0882, T0811 | 8.4.3.1
SR 4.3 | FR 4 - Data confidentiality (DC) | 1 | Use of cryptography | If cryptography is required, the control system shall use cryptographic algorithms, key sizes and mechanisms for key establishment and management according to commonly accept security industry practices and recommendations. | The railway application product supplier should document the practices and procedures relating to cryptographic key establishment and management. The railway application should utilize established and tested encryption and hash algorithms, such as the advanced encryption standards. | 2 - Defend in depth, 6 - Authenticate requests, 8 - Assume secrets not safe | Sup, Sys | Tech, Proc | 1 | TCP/IP Network, Remote Access, Data Storage | T0842, T0887 | 8.5
SR 5.1 | FR 5 - Restricted data flow (RDF) | 1 | Network segmentation | The control system shall provide the capability to logically segment control system networks from non-control system networks and to logically segment critical control system networks from other control system networks. | In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, e.g. dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety-related systems be designed from the beginning to be completely isolated from other networks. | 1 - Secure the weakest link, 2 - Defend in depth | Sys, Op | Tech | 1 | TCP/IP Network | T0800, T0885, T0842 | 9.3
SR 5.1 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | Physical network segmentation | The control system shall provide the capability to physically segment control system networks from non-control system networks and to physically segment critical control system networks from non-critical control system networks. | Independence from non-control networks is required at SR 5.1 RE(1). In case physical segregation is technically not feasible or even an increase in cybersecurity risks, a logical segregation concept is acceptable explicitly if the following associated SRs [SR 1.2, SR 1.8, SR 1.9, SR 3.1/SR 3.1 RE 1, SR 3.7, SR 4.1/SR 4.1 RE 1, SR 6.2, SR 1.5 RE 1] are fulfilled | 1 - Secure the weakest link, 2 - Defend in depth | Sys, Op | Tech | 2 | TCP/IP Network | T0800, T0885, T0842 | 9.3.3.1
SR 5.1 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | Independence from non-railway application networks | The control system shall have the capability to provide network services to control system networks, critical or otherwise, without a connection to non-control system networks. | - | 1 - Secure the weakest link, 2 - Defend in depth | Sup, Sys | Tech | 3 | TCP/IP Network | T0800, T0885, T0842 | 9.3.3.2
SR 5.1 RE(3) | FR 5 - Restricted data flow (RDF) | 4 | Logical and physical isolation of critical networks | The control system shall provide the capability to logically and physically isolate critical control system networks from non-critical control system networks. | The criticality of a railway application is determined by the risk assessment and that should influence the logical and physical isolation. The usage of segmentation methods like different fibres or colours for fibre-optic cables or the usage of cryptographic measures like those mentioned in EN 50159 are ways to implement this requirement in railway applications. | 1 - Secure the weakest link, 2 - Defend in depth | Sup, Sys | Tech | 4 | TCP/IP Network | T0800, T0885, T0842 | 9.3.3.3
SR 5.2 | FR 5 - Restricted data flow (RDF) | 1 | Zone boundary protection | The control system shall provide the capability to monitor and control communications at zone boundaries to enforce the compartmentalization defined in the risk-based zones and conduits model. | - | 1 - Secure the weakest link, 2 - Defend in depth | Op, Sup, Sys | Tech | 1 | TCP/IP Network | T0885, T0822, T0842 | 9.4
SR 5.2 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | Deny by default, allow by exception | The control system shall provide the capability to deny network traffic by default and allow network traffic by exception (also termed deny all, permit by exception). | - | 7 - Control Access | Sup, Sys | Tech | 2 | TCP/IP Network | T0885, T0822, T0842 | 9.4.3.1
SR 5.2 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | Island mode | The control system shall provide the capability to prevent any communication through the control system boundary (also termed island mode). | - | 1 - Secure the weakest link, 2 - Defend in depth | Sup, Sys | Tech | 3 | TCP/IP Network | T0885, T0822, T0842 | 9.4.3.2
SR 5.2 RE(3) | FR 5 - Restricted data flow (RDF) | 3 | Fail close | The control system shall provide the capability to prevent any communication through the control system boundary when there is an operational failure of the boundary protection mechanisms (also termed fail close). This 'fail close' functionality shall be designed such that it does not interfere with the operation of a SIS or other safety-related functions. | Railway safety architectures do not generally permit such behaviours on networks. All essential functions should continue, and non-essential functions stopped in the event of boundary protection violations | 1 - Secure the weakest link, 2 - Defend in depth | Sup, Sys | Tech | 3 | TCP/IP Network | T0885, T0822, T0842 | 9.4.3.3
SR 5.3 | FR 5 - Restricted data flow (RDF) | 1 | General purpose person-to-person communication restrictions | The control system shall provide the capability to prevent general purpose person-to-person messages from being received from users or systems external to the control system. | - | 2 - Defend in depth | Sys | Tech | 2 | TCP/IP Network, Safety Critical | T0839, T0857, T0889 | 9.5
SR 5.3 RE(1) | FR 5 - Restricted data flow (RDF) | 3 | Prohibit all general-purpose person-to-person communications | The control system shall provide the capability to prevent both transmission and receipt of general purpose person-to-person messages. | - | 2 - Defend in depth | Sys | Tech, Tools | 3 | TCP/IP Network, Safety Critical | T0839, T0857, T0889 | 9.5.3.1
SR 5.4 | FR 5 - Restricted data flow (RDF) | 1 | Application partitioning | The control system shall provide the capability to support partitioning of data, applications and services based on criticality to facilitate implementing a zoning model. | - | 2 - Defend in depth | Sys | Tech | 1 | Safety Critical | T0816, T0881, T0838 | 9.6
SR 6.1 | FR 6 - Timely response to events (TRE) | 1 | Audit log accessibility | The control system shall provide the capability for authorized humans and/or tools to access audit logs on a read-only basis. | - | 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access, 9 - Make security usable, 11 - Audit and monitor, 14 - Continuous Protection | Sys, Op | Tech, Proc | 1 | User Interfaces, Remote Access, TCP/IP Network | T0872, T0882, T0863 | 10.3
SR 6.1 RE(1) | FR 6 - Timely response to events (TRE) | 3 | Programmatic access to audit logs | The control system shall provide programmatic access to audit records using an application programming interface (API). | - | 6 - Authenticate requests, 7 - Control access, 9 - Make security usable, 11 - Audit and monitor | Sys, Op | Tech, Proc | 3 | User Interfaces, Remote Access, TCP/IP Network | T0872, T0882, T0863 | 10.3.3.1
SR 6.2 | FR 6 - Timely response to events (TRE) | 2 | Continuous monitoring | The control system shall provide the capability to continuously monitor all security mechanism performance using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner. | - | 6 - Authenticate requests, 7 - Control access, 11 - Audit and monitor, 14 - Continuous Protection | Sys, Op | Tech, Proc, Tools | 2 | TCP/IP Network, Remote Access | T0842, T0887, T0885 | 10.4
SR 7.1 | FR 7 - Resource availability (RA) | 1 | Denial of service protection | The control system shall provide the capability to operate in a degraded mode during a DoS event. | - | 2 - Defend in depth, 7 - Control access | Sys, Sup | Tech, Proc | 1 | TCP/IP Network | T0881, T0816 | 11.3
SR 7.1 RE(1) | FR 7 - Resource availability (RA) | 2 | Manage communication loads | The control system shall provide the capability to manage communication loads (such as using rate limiting) to mitigate the effects of information flooding types of DoS events. | - | 2 - Defend in depth, 7 - Control access | Op, Sys, Sup | Tech, Proc | 2 | TCP/IP Network | T0881, T0816 | 11.3.3.1
SR 7.1 RE(2) | FR 7 - Resource availability (RA) | 3 | Limit DoS effects to other systems or networks | The control system shall provide the capability to restrict the ability of all users (humans, software processes and devices) to cause DoS events which affect other control systems or networks. | - | 2 - Defend in depth, 7 - Control access | Sys, Sup | Tech, Proc | 3 | TCP/IP Network | T0881, T0816 | 11.3.3.2
SR 7.2 | FR 7 - Resource availability (RA) | 1 | Resource management | The control system shall provide the capability to limit the use of resources by security functions to prevent resource exhaustion. | Watchdog based time allocation and scheduling is prevalent in the safety critical railway environment and applications. This is largely applied at monitoring rather than control level. | 2 - Defend in depth, 4 - Grant least privilege, 6 - Authenticate requests, 7 - Control access | Op, Sys, Sup | Tech, Proc | 2 | Operating System, TCP/IP Network | T0881, T0816 | 11.4
SR 7.3 | FR 7 - Resource availability (RA) | 1 | Control system backup | The identity and location of critical files and the ability to conduct backups of user-level and system-level information (including system state information) shall be be supported by the control system without affecting normal plant operations. | Configuration management based on baselines are employed in most railway products. The identity and location of critical files should be known at application level. The ability to conduct backups specifically the critical information and files should be supported by railway application | 3 - Fail secure, 8 - Assume secrets not safe, 14 - Continuous Protection, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 1 | Data Storage, Programmable | T0809, T0836 | 11.5
SR 7.3 RE(1) | FR 7 - Resource availability (RA) | 2 | Backup verification | The control system shall provide the capability to verify the reliability of backup mechanisms. | - | 3 - Fail secure, 8 - Assume secrets not safe, 14 - Continuous Protection, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 2 | Data Storage, Programmable | T0809, T0836 | 11.5.3.1
SR 7.3 RE(2) | FR 7 - Resource availability (RA) | 3 | Backup Automation | The control system shall provide the capability to automate the backup function based on a configurable frequency. | Automate backup based on a configurable frequency | 8 - Assume secrets not safe, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 3 | Data Storage, Programmable | T0809, T0836 | 11.5.3.2
SR 7.4 | FR 7 - Resource availability (RA) | 1 | Control system recovery and reconstitution | The control system shall provide the capability to recover and reconstitute to a known secure state after a disruption or failure. | In view of the safety critical nature, Railways have strict policies on recovery and reconstitution to ensure a safe state in addition to a secure state. A threat risk assessment shall be carried out in order to not breach safety mechanisms for vital data, in case of system recovery from backed up information. | 3 - Fail secure, 8 - Assume secrets not safe, 14 - Continuous Protection, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 1 | Safety Critical, Programmable | T0809, T0889, T0821 | 11.6
SR 7.5 | FR 7 - Resource availability (RA) | 1 | Emergency power | The control system shall provide the capability to switch to and from an emergency power supply without affecting the existing security state or a documented degraded mode. | - | 14 - Continuous Protection | Op | Tech | 1 | Safety Critical | T0816, T0881 | 11.7
SR 7.6 | FR 7 - Resource availability (RA) | 1 | Network and security configuration settings | The control system shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The control system shall provide an interface to the currently deployed network and security configuration settings. | - | 3 - Fail secure, 8 - Assume secrets not safe, 14 - Continuous Protection, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 1 | TCP/IP Network, Wireless Capability | T0885, T0860, T0842 | 11.8
SR 7.6 RE(1) | FR 7 - Resource availability (RA) | 3 | Machine readable reporting of current security settings | The control system shall provide the capability to generate a report listing currently deployed security settings in a machine readable format. | - | 3 - Fail secure, 8 - Assume secrets not safe, 14 - Continuous Protection, 15 - Secure Metadata Management, 16 - Secure Defaults | Op, Sys, Sup | Tech, Proc | 3 | TCP/IP Network, Wireless Capability | T0885, T0860, T0842 | 11.8.3.1
SR 7.7 | FR 7 - Resource availability (RA) | 1 | Least functionality | The control system shall provide the capability to specifically prohibit and/or restrict the use of unnecessary functions, ports, protocols and/or services. | - | 1 - Secure the weakest link, 4 - Grant least privilege, 16 - Secure defaults | Op, Sys, Sup | Tech, Proc | 1 | Programmable, Remote Access | T0871, T0845, T0843 | 11.9
SR 7.8 | FR 7 - Resource availability (RA) | 2 | Control system component inventory | The control system shall provide the capability to report the current list of installed components and their associated properties. | - | 3 - Fail secure, 13 - Precautionary principle | Op, Sys, Sup | Tech, Proc | 1 | All Assets | T0861, T0864 | 11.1

## SR_TTP_Mapping
Security Requirement | FR | SL | Applicable Asset Characteristics | MITRE TTPs Mitigated | Notes | Railway Notes
SR 1.1 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0859, T0812, T0891 | Human user identification and authentication | This includes application interfaces such as web server, file transfer protocol (FTP) server, OPC, and remote desktop interfaces that provide network access to human users and that do not securely convey the authenticated IACS user identity to the application during connection. It is acceptable to implement this requirement in combination with other external authentication solutions including physical security measures in railways.
SR 1.1 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access | T0859, T0812, T0891 | Unique identification and authentication
SR 1.1 RE(2) | FR 1 - Identification and authentication control (IAC) | 3 | User Interfaces, Remote Access, TCP/IP Network | T0859, T0812, T0891 | Multifactor authentication for untrusted networks | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities.
SR 1.1 RE(3) | FR 1 - Identification and authentication control (IAC) | 4 | User Interfaces, Remote Access | T0859, T0812, T0891 | Multifactor authentication for all networks | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities.
SR 1.2 | FR 1 - Identification and authentication control (IAC) | 2 | TCP/IP Network, Programmable | T0800, T0859, T0849 | Identification and authentication of software processes and devices | Note that in the equivalent requirement IEC 62443-2-1 / IEC 62443-2-4 USER-07 "sw services are considered instead of "sw processes": USER-07: All software services shall be identified and authenticated prior to their execution. Identification of internal software processes/services and devices are not a common practice in railway applications or railway systems.
SR 1.2 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | TCP/IP Network, Programmable | T0800, T0859, T0849 | Unique identification and authentication of software processes and devices
SR 1.3 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0859, T0812 | Account management | Railways have mostly a distributed system supported by simple passwords. The full account management requires a major change in the existing control/command and IT infrastructure. The issue of maintenance and multiple commercial contractors complicates the issue.
SR 1.3 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | User Interfaces, Remote Access | T0859, T0812 | Unified account management | The operators should install a unique account and user administration system in combination with physical security in fulfilment of this requirement. The decision for the appropriate solution is left to the operators ideally in a standardized manner across the railway industry.
SR 1.4 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0859, T0891 | Identifier management | An Identifier is a construct (username, tag) which is associated closely to a user or subscriber. Authentication is a procedure based on a secret given by an identified user or subscriber which enable the verification of it, maybe uniquely. There are currently no solutions for railway environments for this requirement as an inherent system solution. Railways have mostly a distributed system supported by simple passwords. Full account management can often only support with an external solution in a form of compensating countermeasures.
SR 1.5 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0812, T0891 | Authenticator management | The password management policy in railways for system administration is normally maintained external to the railway system due to the complexity of distribution of the rail assets and the difficulty of implementing such a policy without central management.
SR 1.5 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access | T0812, T0891 | Protection of authenticators | The protection of authenticators in railway products is managed external to the product by use of operational security measures that include secure delivery and physical security.
SR 1.6 | FR 1 - Identification and authentication control (IAC) | 1 | TCP/IP Network, Remote Access | T0812, T0891 | Wireless access management | Certain railway systems make extensive use of wireless communications such as GSM-R, LTE-R, local WiFi, etc. Wireless access management procedures and methodologies should be considered in this context.
SR 1.7 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0812, T0891 | Strength of password-based authentication | Railway systems that rely on password-based authentication should ensure the strength of the password is appropriate to resist attack.
SR 1.7 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access | T0812, T0891 | Password generation and lifetime restrictions for human users | Railway operators should ensure that provisioning of authenticators for railway systems are performed in accordance with industry best practices.
SR 1.8 | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access, TCP/IP Network | T0849, T0891 | Public key infrastructure (PKI) certificates | In the railway sector, a security model based on a public key infrastructure is not often implemented. If implemented at control level, a clear PKI governance should be defined.
SR 1.9 | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access, TCP/IP Network | T0849, T0891 | Strength of public key authentication | In railway PKI governance should define which certificate type, algorithms and specific key lengths per algorithm are acceptable for railway products.
SR 1.10 | FR 1 - Identification and authentication control (IAC) | 2 | User Interfaces, Remote Access, TCP/IP Network | T0859, T0891 | Authenticator feedback | Feedback and display of authentication information remains a challenge in railway implementations. Where applicable implementation of this requirement should provide clear safety measures and ensure human factors/ergonomics are considered to avoid unintended safety consequences.
SR 1.11 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0859, T0812 | Unsuccessful login attempts | For mission or safety critical systems that deliver essential railway functions, limitation on login attempts may result in system or function unavailability and adversely affect safety. Implementation of this requirement should be fully cognisant of safety and operational availability implications. For example, a freezing of a system (e.g. safe stop in an ETCS Level 2 system) can lead to an unsafe situation. Thus, the required system reaction shall be defined with respect to safety and availability.
SR 1.12 | FR 1 - Identification and authentication control (IAC) | 1 | User Interfaces, Remote Access | T0859, T0891 | System use notification | -
SR 1.13 | FR 1 - Identification and authentication control (IAC) | 1 | TCP/IP Network, Remote Access | T0865, T0822, T0860 | Access via untrusted networks | -
SR 1.13 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | TCP/IP Network, Remote Access | T0865, T0822, T0860 | Explicit access request approval | -
SR 2.1 | FR 2 - Use control (UC) | 1 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | Authorization enforcement | -
SR 2.1 RE(1) | FR 2 - Use control (UC) | 2 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | Authorization enforcement for all users | -
SR 2.1 RE(2) | FR 2 - Use control (UC) | 2 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | Permission mapping to roles | -
SR 2.1 RE(3) | FR 2 - Use control (UC) | 3 | User Interfaces, Remote Access, Programmable | T0800, T0859, T0863 | Supervisor override | Railway operators do not generally have a supervisor to oversee the integrity of their actions and decisions. There is always one person fully responsible for a task (e.g. cab driver for his train running). Supervisor override is common in railways in order to manually accept special situations. These are documented in a juridical way.
SR 2.1 RE(4) | FR 2 - Use control (UC) | 4 | User Interfaces, Remote Access, Programmable, Safety Critical | T0800, T0859, T0863 | Dual approval | This may conflict with time critical activities/functions. In case of such conflicts, this requirement should be implemented with alternative approaches to establish the chain of trust efficiently. For example, changing a set point in the TCMS that can affect the computation of the speed of the train should require a dual approval; bypassing the ETCS control of the speed of the train may require a pre-defined sequence of actions, carefully chosen to minimize the risk of accidental execution, performed by the driver in case of danger.
SR 2.2 | FR 2 - Use control (UC) | 1 | Wireless Capability | T0860, T0887 | Wireless use control | -
SR 2.2 RE(1) | FR 2 - Use control (UC) | 3 | Wireless Capability | T0860, T0887 | Identify and report unauthorized wireless devices | -
SR 2.3 | FR 2 - Use control (UC) | 1 | Remote Access, Wireless Capability | T0864, T0860 | Use control for portable and mobile devices | Portable and mobile devices are already widely used in railway infrastructure. E.g. for diagnostic purposes but also to safety relevant purposes such as shunting / track works. A secure management of mobile access is crucial in the safety critical railway environment.
SR 2.3 RE(1) | FR 2 - Use control (UC) | 3 | Remote Access, Wireless Capability | T0864, T0860 | Enforcement of security status of portable and mobile devices | -
SR 2.4 | FR 2 - Use control (UC) | 1 | Programmable, TCP/IP Network | T0865, T0873 | Mobile code | -
SR 2.4 RE(1) | FR 2 - Use control (UC) | 3 | Programmable, TCP/IP Network | T0865, T0873 | Mobile code integrity check | -
SR 2.5 | FR 2 - Use control (UC) | 1 | User Interfaces | T0882, T0863 | Session lock | In view of the safety critical nature of the railway environment, session locks should be carefully applied so as not to interact adversely with system availability and access to essential functions. For example, the user screen could be locked upon user request or after a configured period of inactivity and require re-authentication if an authorized user wants to unlock it.
SR 2.6 | FR 2 - Use control (UC) | 2 | Remote Access | T0822, T0886 | Remote session termination | -
SR 2.7 | FR 2 - Use control (UC) | 3 | Remote Access, User Interfaces | T0882, T0859 | Concurrent session control | -
SR 2.8 | FR 2 - Use control (UC) | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Auditable events | -
SR 2.8 RE(1) | FR 2 - Use control (UC) | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Centrally managed, system-wide audit trail | Components and sub-systems that log events locally should ensure the monitoring and logging information are transferred to a centrally managed system. There may be a time delay between the local logging data and the transfer to the central system
SR 2.9 | FR 2 - Use control (UC) | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Audit storage capacity | -
SR 2.9 RE(1) | FR 2 - Use control (UC) | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Warn when audit record storage capacity threshold reached | -
SR 2.10 | FR 2 - Use control (UC) | 1 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Response to audit processing failures | -
SR 2.11 | FR 2 - Use control (UC) | 2 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Timestamps | The time source should be protected from unauthorized alteration
SR 2.11 RE(1) | FR 2 - Use control (UC) | 3 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Internal time synchronization | -
SR 2.11 RE(2) | FR 2 - Use control (UC) | 4 | Data Storage, Operating System, TCP/IP Network | T0872, T0882, T0863 | Protection of time source integrity | -
SR 2.12 | FR 2 - Use control (UC) | 3 | User Interfaces, Data Storage | T0859, T0872, T0863 | Non-repudiation for human users | -
SR 2.12 RE(1) | FR 2 - Use control (UC) | 4 | User Interfaces, Data Storage, TCP/IP Network | T0859, T0872, T0863 | Non-repudiation for all users | -
SR 3.1 | FR 3 - System integrity (SI) | 1 | TCP/IP Network, Remote Access | T0800, T0842, T0887 | Communication integrity | -
SR 3.1 RE(1) | FR 3 - System integrity (SI) | 3 | TCP/IP Network, Remote Access | T0800, T0842, T0887 | Cryptographic integrity protection | The cryptographic mechanisms employed should be secure. Rolling stock and restricted network segments with an adequate boundary, intrusion detection and diverse transmission channel (e.g. use of Ethernet and MVB) can use these as compensating countermeasures. Open untrusted networks without compensating countermeasures require this extra protection in railways.
SR 3.2 | FR 3 - System integrity (SI) | 1 | TCP/IP Network, Operating System | T0873, T0865 | Malicious code protection | Prevention means mechanisms such as removable media control, and workstation and laptop management policies, used in conjunction with means of detection at railway system entry points (e.g. USB cleaning stations, IDS, etc.) may be preferred as a compensating security measure from detection mechanisms deployed on all railway embedded devices. Use of USB ports should be strictly limited. When no other solution is available, USB controller and OS driver hardening should be employed to prevent execution of code from USB devices. A secure boot mechanism and a white list application management at operating system/firmware and application layers is required to ensure only authorized software is permitted and executed.
SR 3.2 RE(1) | FR 3 - System integrity (SI) | 2 | TCP/IP Network, Operating System | T0873, T0865 | Malicious code protection on entry and exit points | This RE should be managed at SL1 level to be consistent with SR 3.2 in railways
SR 3.2 RE(2) | FR 3 - System integrity (SI) | 3 | TCP/IP Network, Operating System | T0873, T0865 | Central management and reporting for malicious code protection | Malware and malicious code protection should be centrally managed for integrity and consistency in railways. SIEM protection is largely a dynamic anomaly detection/protection mechanism and may prove inadequate for malicious code protection.
SR 3.3 | FR 3 - System integrity (SI) | 1 | Safety Critical, Programmable | T0889, T0821, T0838 | Security functionality verification | -
SR 3.3 RE(1) | FR 3 - System integrity (SI) | 3 | Safety Critical, Programmable | T0889, T0821, T0838 | Automated mechanisms for security functionality verification | -
SR 3.3 RE(2) | FR 3 - System integrity (SI) | 4 | Safety Critical, Programmable | T0889, T0821, T0838 | Security functionality verification during normal operation | This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems
SR 3.4 | FR 3 - System integrity (SI) | 2 | Firmware Updates, Operating System | T0873, T0857, T0839 | Software and information integrity | -
SR 3.4 RE(1) | FR 3 - System integrity (SI) | 3 | Firmware Updates, Operating System | T0873, T0857, T0839 | Automated notification about integrity violations | -
SR 3.5 | FR 3 - System integrity (SI) | 1 | User Interfaces, Remote Access, Programmable | T0871, T0821 | Input validation | -
SR 3.6 | FR 3 - System integrity (SI) | 1 | Safety Critical, Programmable | T0821, T0838, T0836 | Deterministic output | -
SR 3.7 | FR 3 - System integrity (SI) | 2 | Safety Critical, Programmable | T0816, T0838 | Error handling | -
SR 3.8 | FR 3 - System integrity (SI) | 2 | Remote Access, User Interfaces | T0882, T0822 | Session integrity | -
SR 3.8 RE(1) | FR 3 - System integrity (SI) | 3 | Remote Access, User Interfaces | T0882, T0822 | Invalidation of session IDs after session termination | -
SR 3.8 RE(2) | FR 3 - System integrity (SI) | 3 | Remote Access, User Interfaces | T0882, T0822 | Unique session ID generation | -
SR 3.8 RE(3) | FR 3 - System integrity (SI) | 4 | Remote Access, User Interfaces | T0882, T0822 | Randomness of session IDs | -
SR 3.9 | FR 3 - System integrity (SI) | 2 | Data Storage, TCP/IP Network | T0809, T0872 | Protection of audit information | -
SR 3.9 RE(1) | FR 3 - System integrity (SI) | 4 | Data Storage, TCP/IP Network | T0809, T0872 | Audit records on write-once media | -
SR 4.1 | FR 4 - Data confidentiality (DC) | 1 | TCP/IP Network, Data Storage | T0882, T0842, T0887 | Information confidentiality | -
SR 4.1 RE(1) | FR 4 - Data confidentiality (DC) | 2 | TCP/IP Network, Data Storage, Remote Access | T0882, T0842, T0887 | Protection of confidentiality at rest or in transit via untrusted networks | -
SR 4.1 RE(2) | FR 4 - Data confidentiality (DC) | 4 | TCP/IP Network, Data Storage | T0882, T0842, T0887 | Protection of confidentiality across zone boundaries | -
SR 4.2 | FR 4 - Data confidentiality (DC) | 2 | Data Storage | T0882, T0811 | Information persistence | Current railway applications do not implement extensive permission management so implementation of this requirement for information purging in components and systems is challenging. Read authorization should not be the only criteria for data/information criticality that qualifies for purging.
SR 4.2 RE(1) | FR 4 - Data confidentiality (DC) | 3 | Data Storage | T0882, T0811 | Purging of shared memory resources | -
SR 4.3 | FR 4 - Data confidentiality (DC) | 1 | TCP/IP Network, Remote Access, Data Storage | T0842, T0887 | Use of cryptography | The railway application product supplier should document the practices and procedures relating to cryptographic key establishment and management. The railway application should utilize established and tested encryption and hash algorithms, such as the advanced encryption standards.
SR 5.1 | FR 5 - Restricted data flow (RDF) | 1 | TCP/IP Network | T0800, T0885, T0842 | Network segmentation | In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, e.g. dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety-related systems be designed from the beginning to be completely isolated from other networks.
SR 5.1 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | TCP/IP Network | T0800, T0885, T0842 | Physical network segmentation | Independence from non-control networks is required at SR 5.1 RE(1). In case physical segregation is technically not feasible or even an increase in cybersecurity risks, a logical segregation concept is acceptable explicitly if the following associated SRs [SR 1.2, SR 1.8, SR 1.9, SR 3.1/SR 3.1 RE 1, SR 3.7, SR 4.1/SR 4.1 RE 1, SR 6.2, SR 1.5 RE 1] are fulfilled
SR 5.1 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | TCP/IP Network | T0800, T0885, T0842 | Independence from non-railway application networks | -
SR 5.1 RE(3) | FR 5 - Restricted data flow (RDF) | 4 | TCP/IP Network | T0800, T0885, T0842 | Logical and physical isolation of critical networks | The criticality of a railway application is determined by the risk assessment and that should influence the logical and physical isolation. The usage of segmentation methods like different fibres or colours for fibre-optic cables or the usage of cryptographic measures like those mentioned in EN 50159 are ways to implement this requirement in railway applications.
SR 5.2 | FR 5 - Restricted data flow (RDF) | 1 | TCP/IP Network | T0885, T0822, T0842 | Zone boundary protection | -
SR 5.2 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | TCP/IP Network | T0885, T0822, T0842 | Deny by default, allow by exception | -
SR 5.2 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | TCP/IP Network | T0885, T0822, T0842 | Island mode | -
SR 5.2 RE(3) | FR 5 - Restricted data flow (RDF) | 3 | TCP/IP Network | T0885, T0822, T0842 | Fail close | Railway safety architectures do not generally permit such behaviours on networks. All essential functions should continue, and non-essential functions stopped in the event of boundary protection violations
SR 5.3 | FR 5 - Restricted data flow (RDF) | 1 | TCP/IP Network, Safety Critical | T0839, T0857, T0889 | General purpose person-to-person communication restrictions | -
SR 5.3 RE(1) | FR 5 - Restricted data flow (RDF) | 3 | TCP/IP Network, Safety Critical | T0839, T0857, T0889 | Prohibit all general-purpose person-to-person communications | -
SR 5.4 | FR 5 - Restricted data flow (RDF) | 1 | Safety Critical | T0816, T0881, T0838 | Application partitioning | -
SR 6.1 | FR 6 - Timely response to events (TRE) | 1 | User Interfaces, Remote Access, TCP/IP Network | T0872, T0882, T0863 | Audit log accessibility | -
SR 6.1 RE(1) | FR 6 - Timely response to events (TRE) | 3 | User Interfaces, Remote Access, TCP/IP Network | T0872, T0882, T0863 | Programmatic access to audit logs | -
SR 6.2 | FR 6 - Timely response to events (TRE) | 2 | TCP/IP Network, Remote Access | T0842, T0887, T0885 | Continuous monitoring | -
SR 7.1 | FR 7 - Resource availability (RA) | 1 | TCP/IP Network | T0881, T0816 | Denial of service protection | -
SR 7.1 RE(1) | FR 7 - Resource availability (RA) | 2 | TCP/IP Network | T0881, T0816 | Manage communication loads | -
SR 7.1 RE(2) | FR 7 - Resource availability (RA) | 3 | TCP/IP Network | T0881, T0816 | Limit DoS effects to other systems or networks | -
SR 7.2 | FR 7 - Resource availability (RA) | 1 | Operating System, TCP/IP Network | T0881, T0816 | Resource management | Watchdog based time allocation and scheduling is prevalent in the safety critical railway environment and applications. This is largely applied at monitoring rather than control level.
SR 7.3 | FR 7 - Resource availability (RA) | 1 | Data Storage, Programmable | T0809, T0836 | Control system backup | Configuration management based on baselines are employed in most railway products. The identity and location of critical files should be known at application level. The ability to conduct backups specifically the critical information and files should be supported by railway application
SR 7.3 RE(1) | FR 7 - Resource availability (RA) | 2 | Data Storage, Programmable | T0809, T0836 | Backup verification | -
SR 7.3 RE(2) | FR 7 - Resource availability (RA) | 3 | Data Storage, Programmable | T0809, T0836 | Backup Automation | Automate backup based on a configurable frequency
SR 7.4 | FR 7 - Resource availability (RA) | 1 | Safety Critical, Programmable | T0809, T0889, T0821 | Control system recovery and reconstitution | In view of the safety critical nature, Railways have strict policies on recovery and reconstitution to ensure a safe state in addition to a secure state. A threat risk assessment shall be carried out in order to not breach safety mechanisms for vital data, in case of system recovery from backed up information.
SR 7.5 | FR 7 - Resource availability (RA) | 1 | Safety Critical | T0816, T0881 | Emergency power | -
SR 7.6 | FR 7 - Resource availability (RA) | 1 | TCP/IP Network, Wireless Capability | T0885, T0860, T0842 | Network and security configuration settings | -
SR 7.6 RE(1) | FR 7 - Resource availability (RA) | 3 | TCP/IP Network, Wireless Capability | T0885, T0860, T0842 | Machine readable reporting of current security settings | -
SR 7.7 | FR 7 - Resource availability (RA) | 1 | Programmable, Remote Access | T0871, T0845, T0843 | Least functionality | -
SR 7.8 | FR 7 - Resource availability (RA) | 2 | All Assets | T0861, T0864 | Control system component inventory | -

## Control Assessment Summary
Asset ID | Asset Name | FR 1: IAC | FR 2: UC | FR 3: SI | FR 4: DC | FR 5: RDF | FR 6: TRE | FR 7: RA | Target SL | Custom Controls Needed | Notes
Populate with Assets from Register - will be done after workshop