## Glossary
FR | Fundamental Requirement
SL | Security Level
SR | System Requirement

## Security Levels
| Violation | Means | Resources | Skills | Motivation
SL-0
SL-1 | Casual or Coincidental
SL-2 | Intentional | Simple | Few | Generic | Low
SL-3 |  | Sophisticated | Moderate | Specific | Moderate
SL-4 |  |  | Extended |  | High

## Requirements
Req | FR | SL | Title | Railway notes (informative) | Relevant design principles | Stakeholder | Type | SL1 | SL2 | SL3 | SL4 | IEC62443-3-3 Requirement | IEC62443-3-3 Requirement Text | IEC62443-3-3 Supplemental Guidance
SR 1.1 | FR 1 - Identification and authentication control (IAC) | 1 | Human user identification and authentication | This includes application interfaces such as web server, file transfer protocol (FTP) server, OPC, and remote desktop interfaces that provide network access to human users and that do not securely convey the authenticated IACS user identity to the application during connection. It is acceptable to implement this requirement in combination with other external authentication solutions including physical security measures in railways. | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 5.3 | The control system shall provide the capability to identify and authenticate all human users. This capability shall enforce such identification and authentication on all interfaces which provide human user access to the control system to support segregation of duties and least privilege in accordance with applicable security policies and procedures.
SR 1.1 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | Unique identification and authentication | - | 6 - Authenticate requests 13 - Precautionary principle | Sys Sup | Tech |  | ü | ü | ü | 5.3.3.1 | The control system shall provide the capability to uniquely identify and authenticate all human users.
SR 1.1 RE(2) | FR 1 - Identification and authentication control (IAC) | 3 | Multifactor authentication for untrusted networks | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities. | 6 - Authenticate requests 12 - Proportionality principle | Sys Sup | Tech |  |  | ü | ü | 5.3.3.2 | The control system shall provide the capability to employ multifactor authentication for human user access to the control system via an untrusted network (See 5.15, SR 1.13 - Access via untrusted networks).
SR 1.1 RE(3) | FR 1 - Identification and authentication control (IAC) | 4 | Multifactor authentication for all networks | The feasible multifactor authentication solutions outside the IT system in railways are generally external and could comprise a badge or a physical recognition of presence for the human user e.g. by a phone call. This could equally apply to regularly planned maintenance activities. | 6 - Authenticate requests 12 - Proportionality principle | Op Sys | Tech |  |  |  | ü | 5.3.3.3 | The control system shall provide the capability to employ multifactor authentication for all human user access to the control system.
SR 1.2 | FR 1 - Identification and authentication control (IAC) | 2 | Identification and authentication of software processes and devices | Note that in the equivalent requirement IEC 62443-2-1 / IEC 62443–2-4 USER-07 “sw services are considered instead of “sw processes”: USER-07: All software services shall be identified and authenticated prior to their execution. Identification of internal software processes/services and devices are not a common practice in railway applications or railway systems. | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc |  | ü | ü | ü | 5.4 | The control system shall provide the capability to identify and authenticate all software processes and devices. This capability shall enforce such identification and authentication on all interfaces which provide access to the control system to support least privilege in accordance with applicable security policies and procedures.
SR 1.2 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Unique identification and authentication of software processes and devices | - | 6 - Authenticate requests 12 - Proportionality principle 13 - Precautionary principle | Sys Sup | Tech |  |  | ü | ü | 5.4.3.1 | The control system shall provide the capability to uniquely identify and authenticate all software processes and devices.
SR 1.3 | FR 1 - Identification and authentication control (IAC) | 1 | Account management | Railways have mostly a distributed system supported by simple passwords. The full account management requires a major change in the existing control/command and IT infrastructure. The issue of maintenance and multiple commercial contractors complicates the issue. | 5 - Economize mechanism 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 5.5 | The control system shall provide the capability to support the management of all accounts by authorized users, including adding, activating, modifying, disabling and removing accounts.
SR 1.3 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Unified account management | The operators should install a unique account and user administration system in combination with physical security in fulfilment of this requirement. The decision for the appropriate solution is left to the operators ideally in a standardized manner across the railway industry. | 6 - Authenticate requests 9 - Make security usable | Sys Sup | Tech |  |  | ü | ü | 5.5.3.1 | The control system shall provide the capability to support unified account management.
SR 1.4 | FR 1 - Identification and authentication control (IAC) | 1 | Identifier management | An Identifier is a construct (username, tag) which is associated closely to a user or subscriber. Authentication is a procedure based on a secret given by an identified user or subscriber which enable the verification of it, maybe uniquely. There are currently no solutions for railway environments for this requirement as an inherent system solution. Railways have mostly a distributed system supported by simple passwords. Full account management can often only support with an external solution in a form of compensating countermeasures Example of a compensating countermeasure for rolling stock: Furthermore, for some railway control systems, the capability for the driver or the supervisor to quickly interact with such systems is critical. Local emergency actions for the control system should not be hampered by identification requirements. Access to these systems may be restricted by compensating countermeasures. E.g. drivers can have free access to cab control systems, without need of further identification, once they have entered into the cabin (with a key) and have inserted their driver licence card. On the contrary, they have to identify themselves on their wireless tablet, even if they are inside the cab, because wireless devices can work outside the restricted area, making the countermeasure useless. | 6 - Authenticate requests 9 - Make security usable | Sys Sup | Tech | ü | ü | ü | ü | 5.6 | The control system shall provide the capability to support the management of identifiers by user, group, role or control system interface.
SR 1.5 | FR 1 - Identification and authentication control (IAC) | 1 | Authenticator management | In case a unique authentication management system for the railway system is not feasible, an external solution based on compensating countermeasures should be considered. Example of a compensating countermeasure for rolling stock: A possible solution is to demand the authentication responsibility to the system in charge for identification. E.g. the driver’s card reader not only identifies the driver, but also performs the authentication of the card and do this service for all the subsystems connected to it, which are not able to authenticate the driver but trust the card reader. | 6 - Authenticate requests 8 - Assume secrets not safe 9 - Make security usable | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 5.7 | The control system shall provide the capability to: a) initialize authenticator content; b) change all default authenticators upon control system installation; c) change/refresh all authenticators; and d) protect all authenticators from unauthorized disclosure and modification when stored and transmitted.
SR 1.5 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Hardware security for software process identity credentials | Credentials used as a base of trust shall be storage with Hardware Secure Mechanism. If this for meaningful reasons is not possible the chain of trust should be supported by logically Secure Mechanism plus a compensating countermeasure (e.g. monitoring). | 8 - Assume secrets not safe | Sys Sup | Tech |  |  | ü | ü | 5.7.3.1 | For software process and device users, the control system shall provide the capability to protect the relevant authenticators via hardware mechanisms.
SR 1.6 | FR 1 - Identification and authentication control (IAC) | 1 | Wireless access management | - | 1 - Secure the weakest link 6 - Authenticate requests 7 - Control access 12 - Proportionality principle | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 5.8 | The control system shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication.
SR 1.6 RE(1) | FR 1 - Identification and authentication control (IAC) | 2 | Unique identification and authentication | - | 1 - Secure the weakest link 6 - Authenticate requests 12 - Proportionality principle | Sys Sup | Tech |  | ü | ü | ü | 5.8.3.1 | The control system shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication.
SR 1.7 | FR 1 - Identification and authentication control (IAC) | 1 | Strength of password-based authentication | This will be a big challenge especially for the maintainers. They are used to very simple passwords today and to non-personal (role specific) login. But SR 1.7 is a must because most components cannot be protected against brute force login attempts. In case this requirement cannot be fulfilled the integrity of authentication information should be supported by external means and compensating countermeasures (e.g. use of personal card readers to control access to restricted areas and functions) | 8 - Assume secrets not safe 9 - Make security usable 16 - Secure Defaults | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 5.9 | For control systems utilizing password-based authentication, the control system shall provide the capability to enforce configurable password strength based on minimum length and variety of character types.
SR 1.7 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Password generation and lifetime restrictions for human users | Lifetime restriction for human users is not currently consistently implemented in railways. To support this, an external solution with additional system capability can be used e.g. for authentication control as a compensating countermeasure. | 8 - Assume secrets not safe 9 - Make security usable | Sup | Tech |  |  | ü | ü | 5.9.3.1 | The control system shall provide the capability to prevent any given human user account from reusing a password for a configurable number of generations. In addition, the control system shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform with commonly accepted security industry practices.
SR 1.7 RE(2) | FR 1 - Identification and authentication control (IAC) | 4 | Password lifetime restrictions for all users | In addition, the railway application should enforce password minimum and maximum lifetime restrictions for human user | 6 - Authenticate requests 8 - Assume secrets not safe 9 - Make security usable | Op Sup | Proc Tech |  |  |  | ü | 5.9.3.2 | The control system shall provide the capability to enforce passwork minimum and maxiumum lifetime restrictions for all users.
SR 1.8 | FR 1 - Identification and authentication control (IAC) | 2 | Public Key Infrastructure (PKI) Certificates | - | 8 - Assume secrets not safe 9 - Make security usable | Op Sup | Proc Tech |  | ü | ü | ü | 5.1 | Where PKI is utilized, the control system shall provide the capability to operate a PKI according to commonly accepted best practices or obtain public key certificates from an existing PKI.
SR 1.9 | FR 1 - Identification and authentication control (IAC) | 2 | Strength of public key authentication | In case the given requirements for validation of certificates cannot be supported in railway system, an external solution (e.g. an offline copy of the CA that is updated every 24 h) as compensating countermeasure should be established. | 6 - Authenticate requests 8 - Assume secrets not safe 9 - Make security usable | Op Sys Sup | Tech Proc |  | ü | ü | ü | 5.11 | For control system utilizing public key authentication, the control system shall provide the capability to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate certificates by constructing a certification path to an accepted CA or in the case of self-signed certificates by deploying leaf certificates to all hosts with communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate's revocation status; d) establish user (human, software process or device) control of the corresponding private key; and e) map the authenticated identity to a user (human, softare process or device).
SR 1.9 RE(1) | FR 1 - Identification and authentication control (IAC) | 3 | Hardware security for public key authentication | - | 8 - Assume secrets not safe 9 - Make security usable | Sup | Tech |  |  | ü | ü | 5.11.3.1 | The control system shall provide the capability to protect the relevant private keys via hardware mechanisms according to commonly accepted security industry practices practices and recommendations.
SR 1.10 | FR 1 - Identification and authentication control (IAC) | 1 | Authenticator feedback | - | 8 - Assume secrets not safe 9 - Make security usable | Sys | Tech | ü | ü | ü | ü | 5.12 | The control system shall provide the capability to obscure feedback of authentication information during the authentication process.
SR 1.11 | FR 1 - Identification and authentication control (IAC) | 1 | Unsuccessful login attempts | For mission or safety critical systems that deliver essential railway functions, limitation on login attempts may result in system or function unavailability and adversely affect safety. Implementation of this requirement should be fully cognisant of safety and operational availability implications. For example, a freezing of a system (e.g. safe stop in an ETCS Level 2 system) can lead to an unsafe situation. Thus, the required system reaction shall be defined with respect to safety and availability. | 6 - Authenticate requests 7 - Control access 9 - Make security usable | Op Sys Sup | Tech | ü | ü | ü | ü | 5.13 | The control system shall provide the capability to enforce a limit of a configurable number of consecutive invalid access attempts by any user (human, software process or device) during a configurable time period. The control system shall provide the capability to deny access for a specified period of time or until unlocked by an administrator when this limit has been exceeded. For system accounts on behalf of which critical services or servers are run, the control system shall provide the capability to disallow interactive logons.
SR 1.12 | FR 1 - Identification and authentication control (IAC) | 1 | System use notification | - | 6 - Authenticate requests 9 - Make security usable 10 - Promote privacy | Sys Sup | Tech | ü | ü | ü | ü | 5.14 | The control system shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized personnel.
SR 1.13 | FR 1 - Identification and authentication control (IAC) | 1 | Access via untrusted networks | - | 11 - Audit and monitor | Op Sys Sup | Proc Tech | ü | ü | ü | ü | 5.15 | The control system shall provide the capability to monitor and control all methods of access to the control system via untrusted networks.
SR 1.13 RE (1) | FR 1 - Identification and authentication control (IAC) | 2 | Explicit access request approval | - | 6 - Authenticate requests 13 - Precautionary principle | Op Sys Sup | Proc Tech |  | ü | ü | ü | 5.15.3.1 | The control system shall provide the capability to deny access requests via untrusted networks unless approved by an assigned role.
SR 2.1 | FR 2 - Use control (UC) | 1 | Authorization enforcement | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 6.3 | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all human users for controlling use of the control system to support segregation of duties and least privilege.
SR 2.1 RE(1) | FR 2 - Use control (UC) | 2 | Authorization enforcement for all users | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc |  | ü | ü | ü | 6.3.3.1 | On all interfaces, the control system shall provide the capability to enforce authorizations assigned to all users (humans, software processes and devices) for controlling use of the control system to support segregation of duties and least privilege.
SR 2.1 RE(2) | FR 2 - Use control (UC) | 2 | Permission mapping to roles | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc |  | ü | ü | ü | 6.3.3.2 | The control system shall provide the capability for an authorized user or role to define and modify the mapping of permissions to roles for all human users.
SR 2.1 RE(3) | FR 2 - Use control (UC) | 3 | Supervisor override | Railway operators do not generally have a supervisor to oversee the integrity of their actions and decisions. There is always one person fully responsible for a task (e.g. cab driver for his train running). Supervisor override is common in railways in order to manually accept special situations. These are documented in a juridical way. | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc |  |  | ü | ü | 6.3.3.3 | The control system shall support supervisor manual override of the current human user authorizations for a configurable time or event sequence.
SR 2.1 RE(4) | FR 2 - Use control (UC) | 4 | Dual approval | This may conflict with time critical activities/functions. In case of such conflicts, this requirement should be implemented with alternative approaches to establish the chain of trust efficiently. For example, changing a set point in the TCMS that can affect the computation of the speed of the train should require a dual approval; bypassing the ETCS control of the speed of the train may require a pre-defined sequence of actions, carefully chosen to minimize the risk of accidental execution, performed by the driver in case of danger. | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc |  |  |  | ü | 6.3.3.4 | The control system shall support dual approval where an action can result in serious impact on the industrial process.
SR 2.2 | FR 2 - Use control (UC) | 1 | Wireless use control | - | 5 - Economize mechanism 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech | ü | ü | ü | ü | 6.4 | The control system shall provide the capability to authorize, monitor and enforce usage restrictions for wireless connectivity to the control system according to commonly accepted security industry practices.
SR 2.2 RE(1) | FR 2 - Use control (UC) | 3 | Identify and report unauthorized wireless devices | - | [5 empty] | ü | ü | 6.4.3.1 | The control system shall provide the capability to identify and report unauthorized wireless devices transmitting within the control system physical environment.
SR 2.3 | FR 2 - Use control (UC) | 1 | Use control for portable and mobile devices | Portable and mobile devices are already widely used in railway infrastructure. E.g. for diagnostic purposes but also to safety relevant purposes such as shunting / track works. A secure management of mobile access is crucial in the safety critical railway environment. | 6 - Authenticate requests 7 - Control access 16 - Secure Defaults | Op Sys | Tech Proc | ü | ü | ü | ü | 6.5 | The control system shall provide the capability to automatically enforce configurable usage restrictions that include: a) preventing the use of portable and mobile devices; b) requiring context specific authorization; and c) restricting code and data transfer to/from portable and mobile devices.
SR 2.3 RE(1) | FR 2 - Use control (UC) | 3 | Enforcement of security status of portable and mobile devices | - | [5 empty] | ü | ü | 6.5.3.1 | The control system shall provide the capability to verify that portable or mobile devices attempting to connect to a zone comply with the security requirements of that zone.
SR 2.4 | FR 2 - Use control (UC) | 1 | Mobile code | - | 6 - Authenticate requests 7 - Control access 16 - Secure Defaults | Sys Sup | Tech | ü | ü | ü | ü | 6.6 | The control system shall provide the capability to enforce usage restrictions for mobile code technologies based on the potential to cause damage to the control system that include: a) preventing the execution of mobile code; b) requiring proper authentication and authorization for origin of the code; c) restricting mobile code transfer to/from the control system; and d) monitoring the use of mobile code. | Mobile code technologies include, but are not limited to, Java, JavaScript, ActiveX, PDF, Postscript, Shockwave movies, Flash animations and VBScript.
SR 2.4 RE(1) | FR 2 - Use control (UC) | 3 | Mobile code integrity check | - | [5 empty] | ü | ü | 6.6.3.1 | The control system shall provide the capability to verify integrity of the mobile code before allowing code execution.
SR 2.5 | FR 2 - Use control (UC) | 1 | Session lock | In view of the safety critical nature of the railway environment, session locks should be carefully applied so as not to interact adversely with system availability and access to essential functions. For example, the user screen could be locked upon user request or after a configured period of inactivity and require re-authentication if an authorized user wants to unlock it. | 5 - Economize mechanism 7 - Control access | Op Sys Sup | Tech | ü | ü | ü | ü | 6.7 | The control system shall provide the capability to prevent further access by initiating a session lock after a configurable time period of inactivity or by manual initiation. The session lock shall remain in effect until the human user who owns the session or another authorized human user re-establishes access using appropriate identification and authentication procedures.
SR 2.6 | FR 2 - Use control (UC) | 2 | Remote session termination | - | 5 - Economize mechanism 7 - Control access | Op Sys Sup | Tech |  | ü | ü | ü | 6.8 | The control system shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity or manually by the user who initiated the session.
SR 2.7 | FR 2 - Use control (UC) | 3 | Concurrent session control | - | 5 - Economize mechanism 7 - Control access | Op Sys Sup | Tech Proc |  |  | ü | ü | 6.9 | The control system shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device) to a configurable number of sessions.
SR 2.8 | FR 2 - Use control (UC) | 1 | Auditable events | - | 11 - Audit and monitor | Sys Sup | Tech | ü | ü | ü | ü | 6.1 | The control system shall provide the capability to generate audit records relevant to security for the following categories: access control, request errors, operating system events, control system events, backup and restore events, configuration changes, potential reconnaissance activity and audit log events. Individual audit records shall include the timestamp, source (originating device,software process or human user account), category, type, event ID and event result.
SR 2.8 RE(1) | FR 2 - Use control (UC) | 3 | Centrally managed, system-wide audit trail | Components and sub-systems that log events locally should ensure the monitoring and logging information are transferred to a centrally managed system. There may be a time delay between the local logging data and the transfer to the central system | 11 - Audit and monitor | Sys Sup | Tech |  |  | ü | ü | 6.10.3.1 | The control system shall provide the capability to centrally manage audit events and to compile audit records from multiple components throughout the control system into a system-wide (logical or physical), time-correlated audit trail. The control system shall provide the capability to export these audit records in industry standard formats for analysis by standards commercial log analysis tools, for example, security information and event management (SIEM).
SR 2.9 | FR 2 - Use control (UC) | 1 | Audit storage capacity | - | 11 - Audit and monitor | Sys Sup | Tech | ü | ü | ü | ü | 6.11 | The control system shall allocate sufficient audit record storage capacity according to commonly recognized recommendations for log management and system configuration. The control system shall provide auditing mechanisms to reduce the likelihood of such capacity being exceeded. | Guidelines to be considered could include the NIST Special Publication (SP) 800-92.
SR 2.9 RE(1) | FR 2 - Use control (UC) | 3 | Warn when audit record storage capacity threshold reached | - | 11 - Audit and monitor | Sys Sup | Tech |  |  | ü | ü | 6.11.3.1 | The control system shall provide the capability to issue a warning when the allocated audit record storage volume reaches a configurable percentage of maximum audit record storage capacity.
SR 2.10 | FR 2 - Use control (UC) | 1 | Response to audit processing failures | - | 11 - Audit and monitor | Op Sys Sup | Tech | ü | ü | ü | ü | 6.12 | The control system shall provide the capability to alert personnel and prevent the loss of essential services and functions in the event of an audit procession failure. The control system shall provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations. | Guidelines to be considered when designing appropriate response actions may include the NIST SP800-92
SR 2.11 | FR 2 - Use control (UC) | 2 | Timestamps | - | 11 - Audit and monitor | Sys Sup | Tech |  | ü | ü | ü | 6.13 | The control system shall provide timestamps for use in audit record generation. | The time source should be protected from unauthorized alteration
SR 2.11 RE(1) | FR 2 - Use control (UC) | 3 | Internal time synchronization | - | 11 - Audit and monitor | Sys Sup | Tech |  |  | ü | ü | 6.13.3.1 | The control system shall provide the capability to synchronize internal system clocks at a configurable frequency.
SR 2.11 RE(2) | FR 2 - Use control (UC) | 4 | Protection of time source integrity | - | 11 - Audit and monitor | Sys Sup | Tech |  |  |  | ü | 6.13.3.2 | The time source shall be protected from unauthorized alteration and shall cause an audit event upon alteration.
SR 2.12 | FR 2 - Use control (UC) | 3 | Non-repudiation for human users | - | 6 - Authenticate requests | Op Sys Sup | Tech Proc |  |  | ü | ü | 6.14 | The control system shall provide the capability to determine whether a given human user took a particular action.
SR 2.12 RE(1) | FR 2 - Use control (UC) | 4 | Non-repudiation for all users | - | 6 - Authenticate requests | Op Sys Sup | Tech Proc |  |  |  | ü | 6.14.3.1 | The control system shall provide the capability to determine whether a given user (human, software process or device) took a particular action.
SR 3.1 | FR 3 - System integrity (SI) | 1 | Communication integrity | - | 6 - Authenticate requests 14 - Continuous protection | Sys Sup | Tech | ü | ü | ü | ü | 7.3 | The control system shall provide the capability to protect the integrity of transmitted information.
SR 3.1 RE(1) | FR 3 - System integrity (SI) | 3 | Cryptographic integrity protection | The cryptographic mechanisms employed should be secure. Rolling stock and restricted network segments with an adequate boundary, intrusion detection and diverse transmission channel (e.g. use of Ethernet and MVB) can use these as compensating countermeasures. Open untrusted networks without compensating countermeasures require this extra protection in railways. |  | Sys Sup |  |  |  | ü | ü | 7.3.3.1 | The control system shall provide the capability to employ cryptographic mechanisms to recognize changes to information during communication.
SR 3.2 | FR 3 - System integrity (SI) | 1 | Malicious code protection | Prevention means mechanisms such as removable media control, and workstation and laptop management policies, used in conjunction with means of detection at railway system entry points (e.g. USB cleaning stations, IDS, etc.) may be preferred as a compensating security measure from detection mechanisms deployed on all railway embedded devices. Use of USB ports should be strictly limited. When no other solution is available, USB controller and OS driver hardening should be employed to prevent execution of code from USB devices. A secure boot mechanism and a white list application management at operating system/firmware and application layers is required to ensure only authorized software is permitted and executed. | 1 - Secure the weakest link 2 - Defence-in-depth 11 - Audit and monitor 14 - Continuous Protection 17 - Trusted Components | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 7.4 | The control system shall provide the capability to employ protection mechanisms to prevent, detect, report and mitigate the effects of malicious code or unauthorized software. The control system shall provide the capability to update the protection mechanisms.
SR 3.2 RE(1) | FR 3 - System integrity (SI) | 2 | Malicious code protection on entry and exit points | This RE should be managed at SL1 level to be consistent with SR 3.2 in railways | 7 - Control Access 12 - Proportionality principle | Op Sys Sup | Tech Proc Env |  | ü | ü | ü | 7.4.3.1 | The control system shall provide the capability to employ malicious code protection mechanisms at all entry and exit points.
SR 3.2 RE(2) | FR 3 - System integrity (SI) | 3 | Central management and reporting for malicious codeprotection | Malware and malicious code protection should be centrally managed for integrity and consistency in railways. SIEM protection is largely a dynamic anomaly detection/protection mechanism and may prove inadequate for malicious code protection. | 9 - Make security usable | Op Sys | Tech Proc |  |  | ü | ü | 7.4.3.2 | The control system shall provide the capability to manage malicious code protection mechanisms.
SR 3.3 | FR 3 - System integrity (SI) | 1 | Security functionality verification | - | 3 - Fail secure 11 - Audit and monitor | Sys Sup | Tech | ü | ü | ü | ü | 7.5 | The control system shall provide the capability to support verification of the intended operation of security functions and report when anomalies are discovered during FAT, SAT and scheduled maintenance. These security functions shall include all those necessary to support the security requirements specified in this standard.
SR 3.3 RE(1) | FR 3 - System integrity (SI) | 3 | Automated mechanisms for security functionality verification | - | 9 - Make security usable | Sys Sup | Tech Proc |  |  | ü | ü | 7.5.3.1 | The control system shall provide the capability to employ automated mechanisms to support management of security verification during FAT, SAT and scheduled maintenance.
SR 3.3 RE (2) | FR 3 - System integrity (SI) | 4 | Security functionality verification during normal operation | This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems | 9 - Make security usable | Sys | Tech Proc |  |  |  | ü | 7.5.3.2 | The control system shall provide the capability to support verification of the intended operation of security functions during normal operations.
SR 3.4 | FR 3 - System integrity (SI) | 2 | Software and information integrity | - | 8 - Assume secrets not safe 11 - Audit and monitor 13 - Precautionary principle | Sys Sup | Tech |  | ü | ü | ü | 7.6 | The control system shall provide the capability to detect, record, report and protect against unauthorized changes to software and information at rest.
SR 3.4 RE(1) | FR 3 - System integrity (SI) | 3 | Automated notification about integrity violations | - | 9 - Make security usable 14 - Continuous Protection | Sup | Tech |  |  | ü | ü | 7.6.3.1 | The control system shall provide the capability to use automated tools that provide notification to a configurable set of recipients upon discovering discrepancies during integrity verification.
SR 3.5 | FR 3 - System integrity (SI) | 1 | Input validation | - | 2 - Defence-indepth 7 - Control Access 14 - Continuous Protection | Sup | Tech | ü | ü | ü | ü | 7.7 | The control system shall validate the syntax and content of any input which is used as an industrial process control input or input that directly impacts the action of the control system.
SR 3.6 | FR 3 - System integrity (SI) | 1 | Deterministic output | - | 3 - Fail secure 12 - Proportionality principle 13 - Precautionary principle | Sys Sup | Tech Proc | ü | ü | ü | ü | 7.8 | The control system shall provide the capability to set outputs to a predetermined state if normal operation cannot be maintained as a result of an attack.
SR 3.7 | FR 3 - System integrity (SI) | 2 | Error handling | - | 9 - Make security usable 10 - Promote privacy 11 - Audit and monitor | Sys Sup | Tech Proc |  | ü | ü | ü | 7.9 | The control system shall identify and handle error conditions in a manner such that effective remediation can occur. This shall be done in a manner which does not provide information that could be exploited by adversaries to attack the IACS unless revealing this information is necessary for the timely troubleshooting of problems.
SR 3.8 | FR 3 - System integrity (SI) | 2 | Session integrity | - | 6 - Authenticate requests 7 - Control Access | Sup | Tech |  | ü | ü | ü | 7.1 | The control system shall provide the capability to protect the integrity of sessions. The control system shall reject any usage of invalid session IDs.
SR 3.8 RE(1) | FR 3 - System integrity (SI) | 3 | Invalidation of session IDs after session termination | - | 9 - Make security usable | Sup | Tech Op |  |  | ü | ü | 7.10.3.1 | The control system shall provide the capability to invalidate session IDs upon user logout or other session termination (including browser sessions).
SR 3.8 RE(2) | FR 3 - System integrity (SI) | 3 | Unique session ID generation | - |  | Sup | Tech |  |  | ü | ü | 7.10.3.2 | The control system shall provide the capability to generate a unique session ID for each session and treat all unexpected session IDs as invalid.
SR 3.8 RE(3) | FR 3 - System integrity (SI) | 4 | Randomness of session Ids | - |  | Sup | Tech |  |  |  | ü | 7.10.3.3 | The control system shall provide the capability to generate unique session IDs with commonly accepted sources of randomness.
SR 3.9 | FR 3 - System integrity (SI) | 2 | Protection of audit information | - | 4 - Grant least privilege | Sys Sup | Tech |  | ü | ü | ü | 7.11 | The control system shall protect audit information and audit tools (if present) from unauthorized access, modification and deletion.
SR 3.9 RE(1) | FR 3 - System integrity (SI) | 4 | Audit records on write-once media | - | 13 - Precautionary principle | Sup | Tech |  |  |  | ü | 7.11.3.1 | The control system shall provide the capability to produce audit records on hardware-enforced write-once media.
SR 4.1 | FR 4 - Data confidentiality (DC) | 1 | Information confidentiality | - | 4 - Grant least privilege 8 - Assume secrets not safe 15 - Secure Metadata Management 16 - Secure Defaults | Sup Sys | Tech | ü | ü | ü | ü | 8.3 | The control system shall provide the capability to protect the confidentiality of information for which explicit read authorization is supported, whether at rest or in transit.
SR 4.1 RE(1) | FR 4 - Data confidentiality (DC) | 2 | Protection of confidentiality at rest or in transit via untrusted networks | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access 8 - Assume secrets not safe 10 - Promote privacy | Sys Op | Tech Proc |  | ü | ü | ü | 8.3.3.1 | The control system shall provide the capability to protect the confidentiality of information at rest and remote access sessions traversing an untrusted network.
SR 4.1 RE(2) | FR 4 - Data confidentiality (DC) | 4 | Protection of confidentiality across zone boundaries | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access 8 - Assume secrets not safe 10 - Promote privacy | Sup Sys | Tech Proc |  |  |  | ü | 8.3.3.2 | The control system shall provide the capability to protect the confidentiality of information traversing any zone boundary.
SR 4.2 | FR 4 - Data confidentiality (DC) | 2 | Information persistence | Current railway applications do not implement extensive permission management so implementation of this requirement for information purging in components and systems is challenging. Read authorization should not be the only criteria for data/information criticality that qualifies for purging. | 7 - Control access 15 - Secure Metadata Management 16 - Secure Defaults | Sup Sys Op | Tech Proc |  | ü | ü | ü | 8.4 | The control system shall provide the capability to purge all informatino for which explicit read authorization is supported from components to be released from active service and/or decommissioned.
SR 4.2 RE(1) | FR 4 - Data confidentiality (DC) | 3 | Purging of shared memory resources | - | 8 - Assume secrets not safe | Op |  |  |  | ü | ü | 8.4.3.1 | The control system shall provide the capability to prevent unauthorized and unintended information transfer via volatile shared memory resources.
SR 4.3 | FR 4 - Data confidentiality (DC) | 1 | Use of cryptography | The railway application product supplier should document the practices and procedures relating to cryptographic key establishment and management. The railway application should utilize established and tested encryption and hash algorithms, such as the advanced encryption standards. | 2 - Defend in depth 6 - Authenticate requests 8 - Assume secrets not safe | Sup Sys | Tech Proc | ü | ü | ü | ü | 8.5 | If cryptography is required, the control system shall use cryptographic algorithms, key sizes and mechanisms for key establishment and management according to commonly accept security industry practices and recommendations. | Generally accepted practices and recommendations can be found in documents such as NIST SP800-57. Implementation requirements can be found for example in ISO/IEC 19790
SR 5.1 | FR 5 - Restricted data flow (RDF) | 1 | Network segmentation | In response to an incident, it may be necessary to break the connections between different network segments. In that event, the services necessary to support essential operations should be maintained in such a way that the devices can continue to operate properly and/or shutdown in an orderly manner. This may require that some servers may need to be duplicated on the control system network to support normal network features, e.g. dynamic host configuration protocol (DHCP), domain name service (DNS) or local CAs. It may also mean that some critical control systems and safety-related systems be designed from the beginning to be completely isolated from other networks. | 1 - Secure the weakest link 2 - Defend in depth | Sys Op | Tech | ü | ü | ü | ü | 9.3 | The control system shall provide the capability to logically segment control system networks from non-control system networks and to logically segment critical control system networks from other control system networks.
SR 5.1 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | Physical network segmentation | Independence from non-control networks is required at SR 5.1 RE(1). In case physical segregation is technically not feasible or even an increase in cybersecurity risks, a logical segregation concept is acceptable explicitly if the following associated SR’s [SR 1.2, SR 1.8, SR 1.9, SR 3.1/SR 3.1 RE 1, SR 3.7, SR 4.1/SR 4.1 RE 1, SR 6.2, SR 1.5 RE 1] are fulfilled | 1 - Secure the weakest link 2 - Defend in depth | Sys Op | Tech |  | ü | ü | ü | 9.3.3.1 | The control system shall provide the capability to physically segment control system networks from non-control system networks and to physically segment critical control system networks from non-critical control system networks.
SR 5.1 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | Independence from nonrailway application networks | - | 1 - Secure the weakest link 2 - Defend in depth | Sup Sys | Tech |  |  | ü | ü | 9.3.3.2 | The control system shall have the capability to provide network services to control system networks, critical or otherwise, without a connection to non-control system networks.
SR 5.1 RE(3) | FR 5 - Restricted data flow (RDF) | 4 | Logical and physical isolation of critical networks | The criticality of a railway application is determined by the risk assessment and that should influence the logical and physical isolation. The usage of segmentation methods like different fibres or colours for fibre-optic cables or the usage of cryptographic measures like those mentioned in EN 50159 are ways to implement this requirement in railway applications. | 1 - Secure the weakest link 2 - Defend in depth | Sup Sys | Tech |  |  |  | ü | 9.3.3.3 | The control system shall provide the capability to logically and physically isolate critical control system networks from non-critical control system networks.
SR 5.2 | FR 5 - Restricted data flow (RDF) | 1 | Zone boundary protection | - | 1 - Secure the weakest link 2 - Defend in depth | Op Sup Sys | Tech | ü | ü | ü | ü | 9.4 | The control system shall provide the capability to monitor and control communications at zone boundaries to enforce the compartmentalization defined in the risk-based zones and conduits model.
SR 5.2 RE(1) | FR 5 - Restricted data flow (RDF) | 2 | Deny by default, allow by exception | - | 7 - Control Access | Sup Sys | Tech |  | ü | ü | ü | 9.4.3.1 | The control system shall provide the capability to deny network traffic by default and allow network traffic by exception (also termed deny all, permit by exception).
SR 5.2 RE(2) | FR 5 - Restricted data flow (RDF) | 3 | Island mode | - |  |  | Tech |  |  | ü | ü | 9.4.3.2 | The control system shall provide the capability to prevent any communication through the control system boundary (also termed island mode).
SR 5.2 RE(3) | FR 5 - Restricted data flow (RDF) | 3 | Fail close | Railway safety architectures do not generally permit such behaviours on networks. All essential functions should continue, and non-essential functions stopped in the event of boundary protection violations |  |  | Tech |  |  | ü | ü | 9.4.3.3 | The control system shall provide the capability to prevent any communication through the control system boundary when there is an operational failure of the boundary protection mechanisms (also termed fail close). This 'fail close' functionality shall be designed such that it does not interfere with the operation of a SIS or other safety-related functions.
SR 5.3 | FR 5 - Restricted data flow (RDF) | 1 | General purpose person-to-person communication restrictions | - | 2 - Defend in depth | Sys | Tech | ü | ü | ü | ü | 9.5 | The control system shall provide the capability to prevent general purpose person-to-person messages from being received from users or systems external to the control system.
SR 5.3 RE(1) | FR 5 - Restricted data flow (RDF) | 3 | Prohibit all general-purpose person-to- person communications | - |  | Sys | Tech Tools |  |  | ü | ü | 9.5.3.1 | The control system shall provide the capability to prevent both transmission and receipt of general purpose person-to-person messages.
SR 5.4 | FR 5 - Restricted data flow (RDF) | 1 | Application partitioning | - |  |  | Tech | ü | ü | ü | ü | 9.6 | The control system shall provide the capability to support paritioning of data, applications and services based on criticality to facilitate implementing a zoning model.
SR 6.1 | FR 6 - Timely response to events (TRE) | 1 | Audit log accessibility | - | 4 - Grant least privilege 6 - Authenticate requests 7 - Control access 9 - Make security usable 11 - Audit and monitor 14 - Continuous Protection | Sys Op | Tech Proc | ü | ü | ü | ü | 10.3 | The control system shall provide the capability for authorized humans and/or tools to access audit logs on a read-only basis.
SR 6.1 RE(1) | FR 6 - Timely response to events (TRE) | 3 | Programmatic access to audit logs | - | 6 - Authenticate requests 7 - Control access 9 - Make security usable 11 - Audit and monitor | Sys Op | Tech Proc |  |  | ü | ü | 10.3.3.1 | The control system shall provide programmatic access to audit records using an application programming interface (API).
SR 6.2 | FR 6 - Timely response to events (TRE) | 2 | Continuous monitoring | - | 6 - Authenticate requests 7 - Control access 11 - Audit and monitor 14 - Continuous Protection | Sys Op | Tech Proc Tools |  | ü | ü | ü | 10.4 | The control system shall provide the capability to continuously monitor all security mechanism performance using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner.
SR 7.1 | FR 7 - Resource availability (RA) | 1 | Denial of service protection | - | 2 - Defend in depth 7 - Control access | Sys Sup | Tech Proc | ü | ü | ü | ü | 11.3 | The control system shall provide the capability to operate in a degraded mode during a DoS event.
SR 7.1 RE(1) | FR 7 - Resource availability (RA) | 2 | Manage communication loads | - | 2 - Defend in depth 7 - Control access | Op Sys Sup | Tech Proc |  | ü | ü | ü | 11.3.3.1 | The control system shall provide the capability to manage communication loads (such as using rate limiting) to mitigate the effects of information flooding types of DoS events.
SR 7.1 RE(2) | FR 7 - Resource availability (RA) | 3 | Limit DoS effects to other systems or networks | - | 2 - Defend in depth 7 - Control access | Sys Sup | Tech Proc |  |  | ü | ü | 11.3.3.2 | The control system shall provide the capability to restrict the ability of all users (humans, software processes and devices) to cause DoS events which affect other control systems or networks.
SR 7.2 | FR 7 - Resource availability (RA) | 1 | Resource management | Watchdog based time allocation and scheduling is prevalent in the safety critical railway environment and applications. This is largely applied at monitoring rather than control level. | 2 - Defend in depth 4 - Grant least privilege 6 - Authenticate requests 7 - Control access | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 11.4 | The control system shall provide the capability to limit the use of resources by securty functions to prevent resource exhaustion.
SR 7.3 | FR 7 - Resource availability (RA) | 1 | Control system backup | Configuration management based on baselines are employed in most railway products. The identity and location of critical files should be known at application level. The ability to conduct backups specifically the critical information and files should be supported by railway application | 3 - Fail secure 8 - Assume secrets not safe 14 - Continuous Protection 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 11.5 | The identity and location of critical files and the ability to conduct backups of user-level and system-level information (including system state information) shall be be supported by the contol system without affecting normal plant operations.
SR 7.3 RE(1) | FR 7 - Resource availability (RA) | 2 | Backup verification | - | 3 - Fail secure 8 - Assume secrets not safe 14 - Continuous Protection 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc |  | ü | ü | ü | 11.5.3.1 | The control system shall provide the capability to verify the reliability of backup mechanisms.
SR 7.3 RE(2) | FR 7 - Resource availability (RA) | 3 | Backup Automation | Automate backup based on a configurable frequency | 8 - Assume secrets not safe 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc |  |  | ü | ü | 11.5.3.2 | The control system shall provide the capability to automate the backup function based on a configurable frequency.
SR 7.4 | FR 7 - Resource availability (RA) | 1 | Control system recovery and reconstitution. | In view of the safety critical nature, Railways have strict policies on recovery and reconstitution to ensure a safe state in addition to a secure state. A threat risk assessment shall be carried out in order to not breach safety mechanisms for vital data, in case of system recovery from backed up information. | 3 - Fail secure 8 - Assume secrets not safe 14 - Continuous Protection 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 11.6 | The control system shall provide the capability to recover and reconstitute to a known secure state after a disruption or failure.
SR 7.5 | FR 7 - Resource availability (RA) | 1 | Emergency power | - | 14 - Continuous Protection | Op | Tech | ü | ü | ü | ü | 11.7 | The control system shall provide the capability to switch to and from an emergency power supply without affecting the existing security state or a documented degraded mode.
SR 7.6 | FR 7 - Resource availability (RA) | 1 | Network and security configuration settings | - | 3 - Fail secure 8 - Assume secrets not safe 14 - Continuous Protection 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 11.8 | The control system shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The control system shall provide an interface to the currently deployed network and security configuration settings.
SR 7.6 RE(1) | FR 7 - Resource availability (RA) | 3 | Machine readable reporting of current security settings | - | 3 - Fail secure 8 - Assume secrets not safe 14 - Continuous Protection 15 - Secure Metadata Management 16 - Secure Defaults | Op Sys Sup | Tech Proc |  |  | ü | ü | 11.8.3.1 | The control system shall provide the capability to generate a report listing currently deployed security settings in a machine readable format.
SR 7.7 | FR 7 - Resource availability (RA) | 1 | Least functionality | - | 1 - Secure the weakest link 4 - Grant least privilege 16 - Secure defaults | Op Sys Sup | Tech Proc | ü | ü | ü | ü | 11.9 | The control system shall provide the capability to specifically prohibit and/or restrict the use of unnecessary functions, ports, protocols and/or services.
SR 7.8 | FR 7 - Resource availability (RA) | 2 | Control system component inventory | - | 3 - Fail secure 13 - Precautionary principle | Op Sys Sup | Tech Proc |  | ü | ü | ü | 11.1 | The control system shall provide the capability to report the current list of installed components and their associated properties.